# SECTION 26 32 13

# ENGINE GENERATOR

PART 1 GENERAL

- SUMMARY

  - This section includes the following items from a single supplier:

    - Engine Generator Set.

    - Enclosure.

    - Diesel and DEF Tanks (diesel fuel and DEF supplied by owner).

    - Trailer.

    - Related Accessories as specified.

  - Products Furnished or Supplied but not installed.

  - Related Requirements

    - It is the intent of this specification to secure an engine-driven generator set that has been prototype tested, factory built, production-tested, and site-tested together with all accessories necessary for a complete system as shown on the plans and drawings and specified herein. The equipment supplied shall meet the requirements of the National Electrical Code and applicable local codes and regulations.

    - Any exceptions to the published specifications shall be subject to the approval of the engineer and submitted minimum 10 days prior to the closing  of the bid with a line by line summary description of all the items of compliance, any items that have been are omitted or have been taken exception to, and a complete description of all deviations.

    - All equipment shall be new and of current production by an international, power system manufacturer of generators, transfer switches, and paralleling switchgear.  The manufacturer shall be a supplier of a complete and coordinated system. There will be single-source responsibility for warranty, parts, and service through a factory-authorized representative with factory-trained technicians.

- SUBMITTALS

  - Action Submittals

    - Product Data

      - The submittal shall include prototype test certification and specification sheets showing all standard and optional accessories to be supplied; schematic wiring diagrams, dimension drawings, and interconnection diagrams identifying by terminal number each required interconnection between the generator set, the transfer switch, and the remote annunciator panel if it is included elsewhere in these specifications.

    - Shop Drawings.

  - Informational Submittal

    - Certificates.

    - Test and Evaluation Reports.

    - Manufacturer’s Instruction.

    - Field or Site Quality Control.

    - Manufacturer’s Report.

    - Special Procedure Submittal.

  - Closeout Submittal.

    - Maintenance Contracts.

    - Operation and Maintenance Data.

    - Warranty Documentation.

    - Software.

- Quality Assurance

  - Regulatory Agency

    - The generator set shall conform to the requirements of the following codes and standards:

      - CSA C22.2, No. 14-M91 Industrial Control Equipment.

      - EN50082-2, Electromagnetic Compatibility-Generic Immunity Requirements, Part 2: Industrial.

      - EN55011, Limits and Methods of Measurement of Radio Interference Characteristics of Industrial, Scientific and Medical Equipment.

      - IEC8528 part 4, Control Systems for Generator Sets.

      - IEC Std 61000-2 and 61000-3 for susceptibility, 61000-6 radiated and conducted electromagnetic emissions.

      - IEEE446 Recommended Practice for Emergency and Standby Power Systems for Commercial and Industrial Applications.

      - NFPA 70, National Electrical Code.

      - NFPA 110, Emergency and Standby Power Systems.

    - Qualifications

      - The equipment shall be produced by a manufacturer who is ISO 9001 certified for the design, development, production and service of its complete product line.

      - The power system shall be produced by a manufacturer who has produced this type of equipment for a period of at least 10 years and who maintains a service organization available twenty-four hours a day throughout the year.

    - Manufacturers

      - The power system shall be furnished by a single manufacturer who shall be responsible for the design, coordination, and testing of the complete system.  The entire system shall be supplied as shown on the plans, drawings, and specifications herein.

- Field or Site Conditions

  - Ambient Conditions

    - Engine- generator set shall operate in the following conditions without any damage to the unit or its loads.

      - Ambient Temperature:  77 °F

      - Altitude : 500 ft

      - Relative Humidity:  95%

- Warranty

  - Manufacturer’s Warranty

    - The generator set shall include a standard warranty covering three (3) year or 3000 hours, whichever occurs first, to guarantee against defective material and workmanship in accordance with the manufacturer's published warranty from the date of initial startup.

    - The trailer has a standard warranty covering one (1) year or 3000 hours, whichever occurs first, to guarantee against defective material and workmanship in accordance with the manufacturer's published warranty from the date of initial startup.

    - The generator set manufacturer and its distributor shall maintain a 24-hour parts and service organization.  This organization shall regularly engage in maintenance contract programs to perform preventive maintenance and service on equipment similar to that specified.  A service agreement shall be available and shall include system operation under simulated operating conditions; adjustment to the generator set, transfer switch, and switchgear controls as required, and certification in the owner's maintenance log of repairs made and functional tests performed on all systems.

PART 2 PRODUCTS

- Equipment

  - Equipment

    - The generator set shall be a Kohler model 120REOZT4 with a 4R12X alternator, 3-phase, 60Hz and 0.8 power factor, Prime Power rated at (select one a-f):

a. 120/208 volts, 120.0 kVA and 96.0kW

b. 120/240 volts, 116.0kVA and 93.0kw

c. 277/480 volts, 120.0kva and 96.0kw

d. 347/600 volts, 120.0kva and 96.0kw

e. 120/240 volts, single-phase at 1.0pf, 90.0kva and 90.0kw

f. 3-position selector switch with 120/208v, 277/480v 3-phase and 120/240v 1-phase.

The generator set shall be capable of a 150°C Standby rating while operating in an ambient condition of less than or equal to 77 °F and a maximum elevation of 500 ft above sea level. The standby rating shall be available for the duration of the outage.

  - Engine

    - The minimum 4.5-liter displacement engine shall deliver a minimum of 166 HP at a governed engine speed of 1800 rpm, and shall be equipped with the following:

      - Isochronous governor capable of 0.5% steady-state frequency regulation

      - 12-volt positive-engagement solenoid shift-starting motor

      - 90-ampere automatic battery charging alternator with a solid-state voltage regulation

      - Positive displacement, full-pressure lubrication oil pump, cartridge oil filters, dipstick, and oil drain

      - Dry-type replaceable heavy-duty air cleaner with air cleaner restriction indicator

      - Engine-driven or electric fuel-transfer pump including fuel filter and electric solenoid fuel shutoff valve capable of lifting fuel

      - The turbocharged engine shall be fueled by diesel

      - The engine shall have a minimum of 4 cylinders and be liquid-cooled

    - The engine shall be EPA certified to Tier 4 Final non-road standards from the factory

    - The engine shall be equipped with cooled Exhaust Gas Regeneration (EGR), Diesel Oxidation Catalyst (DOC) and a Diesel Particulate Filter (DPF) to meet Tier 4 Final.

    - The generator must accept rated load in one-step.

    - Unit shall include appropriate amounts of engine oil and antifreeze.

  - Cooling System

    - The engine shall be liquid-cooled by a closed loop, unit mounted radiator rated to operate the generator set at full load at an ambient temperature of 45 degrees C (113 degrees F) at the prime rating.  The radiator fan and other rotating engine parts shall be guarded against accidental contact.

  - Heavy Duty Air Cleaner

- The air cleaner shall provide engine air filtration which meets the engine manufacturer's specifications under typical operating conditions.

  - Battery

    - Each genset requires a maintenance free BCI group 24 battery which must meet the engine manufactures' specifications for the ambient conditions specified in Part 1 Project Conditions and shall comply with the NFPA requirements for engine cranking cycles.  This battery shall be rated according to SAE Standards J-537 with a minimum cold cranking amp of 450 amps and a minimum reserve capacity of 120 Minutes at 80F.  The battery plates shall be constructed of a Calcium-Lead alloy to provide long waterless operation and extended battery life. The battery must contain a handle to aid in lifting and the case must be constructed of polypropylene to resist breakage and extend service life

    - Battery rack and battery cables capable of holding the manufacturer's recommended batteries shall be supplied.

    - Lockable battery disconnect switch.

  - Trailer

    - The generator set shall be equipped with a heavy-duty, dual-axle trailer that has been designed for highway towing, as well as off-road transportation of the engine generator set, fuel, and all accessories.

    - The dual-axle trailer shall have a Gross Vehicle Weight Rating (GVWR) of at least 10,000 lbs. The trailer shall have sufficient rating to carry the engine generator set, fuel, and all accessories.

    - The trailer frame shall be welded 2" x 4" steel tube construction, with 2" x 4" steel tube cross-members located for mounting the engine generator set.   Fenders and decking shall be constructed to support 500#s.

    - The trailer shall have two-part powder paint system, primer and black top coat to meet 1,000-hour salt spray test ASTM #B-117.

    - ST225/75R15, load range D tires shall be mounted on 6-lug, 15x6 conventional steel wheels.

    - The trailer hitch height shall be adjustable and be equipped with a 2 5/16" ball coupler and 3" Lunette eye coupler.

    - The trailer shall be equipped with a tongue jack.

    - Heavy-duty safety chains with slip hooks and safety latches shall be provided.

    - The trailer incorporates a breakaway switch and battery to actuate the trailer brakes should a trailer breakaway occur.

    - Trailer lighting and reflectors shall meet DOT regulations. Running lights shall be recessed into the frame rails to prevent accidental breakage. Provide with 7-pin harness and connector for the towing vehicle.

    - Trailer shall be equipped with a factory-mounted, lockable steel toolbox containing a fire extinguisher.   The lock shall use the same key as the enclosure.

    - Lockable spare tire mounted on trailer.

  - Enclosure

    - Durable steel, sound-attenuating housing with quiet operation of 71 dB(A) log average @ 7 m (23 ft.) with full load at the prime rating.

    - Stainless steel hinges and lockable latches on doors.

    - Single-point lifting eye and four-point tie down system.

    - Enclosures shall be equipped with sufficient side and end doors to allow access for operation, inspection, and service of the unit and all options.  When the generator set controller faces the rear of the generator set, an additional rear facing door is required.

    - A bulkhead wall at the radiator to prevent recirculation of hot air.

    - The complete exhaust system shall be internal to the enclosure.

    - The acoustic insulation shall be fixed to the mounting surface with pressure sensitive adhesive.  The acoustical insulation shall be flame retardant and UL 94-HB recognized.

    - Enclosure designed to direct cooling discharge air in a vertical direction.

    - Oil drain extension brought out to the edge of the skid for easy of changing oil.

The enclosure shall have powder paint to meet 1,000-hour salt spray test ASTM B-117.

The enclosure shall be finish coated with powder baked paint for superior finish, durability and appearance.  Enclosures will be finished in white.

  - Fuel oil storage

    - Subbase fuel tank for 24-hour run time (192 gal) with full load at prime rating.

    - Fuel tank includes the fuel level gauge, fuel fill with lockable cap, and an atmospheric vent.

    - The secondary containment tank’s construction protects against fuel leaks or ruptures. The inner (primary) tank is sealed inside the outer (secondary) tank. The outer tank contains the fuel if the inner tank leaks or ruptures.

    - 125% environmental containment basin for oil and coolant.

    - 110% secondary containment tank for fuel.

    - Unit fuel fill shall be an external 2" NPT opening.  Fuel fill shall be lockable.

    - Tank shall have external fill and drain ports for use with external tank.

    - Emergency venting on secondary containment shall be standard.

  - Controller

    - Decision-Maker® 3500 Generator Set Controller with paralleling capabilities, bus sensing, first-on-logic, synchronizer, (isochronous, droop and external bias control) plus load sharing.

  - The generator set controller shall be a microprocessor based control system that will provide automatic starting, system monitoring, and protection. The controller system shall also provide local monitoring and remote monitoring. The control system shall be capable of PC based updating of all necessary parameters, firmware, and software.

  - The controller shall be mounted on the generator set and shall have integral vibration isolation. The controller shall be prototype and reliability tested to ensure operation in the conditions encountered.

    - Codes and Standards

- The generator set controller shall meet NFPA 110 requirements and shall include an integral alarm horn as required by NFPA.

- The controller shall meet NEC requirements.

- The controller shall be UL 508 or UL 6200 listed.

    - Applicability

- The controller shall be a standard offering in the manufacturer's controller product line.

- The controller shall support 12-volt and 24volt starting systems.

- The controller's environmental specification shall be: -40°C to 70°C operating temperature range and 5-95% humidity, non-condensing.

- The controller shall mount on the generator.

    - Controller Buttons, Display and Components

- The generator set controller shall include the following features and functions:

- Push button Master Control buttons. The buttons shall be tactile-feel membrane with an indicator light to initiate the following functions:

  - Run Mode: When in the run mode the generator set shall start as directed by the operator.

  - Off/Reset Mode: When in the Off/Reset mode the generator set shall stop, the reset shall reset all faults, allowing for the restarting of the generator set after a shutdown.

  - Auto Mode: When in Auto the mode the generator set shall be ready to accept a signal from a remote device.

- Emergency Stop Switch. The emergency stop switch shall be red in color with a "mushroom" type head. Depressing the stop button will immediately stop the generator set and lockout the generator set for any automatic remote starting.

- Push Button/Rotary Selector dial. This dial shall be used for selection of all Menus and sub-menus. Rotating the dial moves you through the menus, pushing the dial selects the menu and function/features in that menu. Pushing the button selects the feature/function and sub-menus.

- Digital Display.  The display shall have back lighting for ease of operator use in high and low light conditions. The display shall display status of all faults and warnings. The display shall also display any engine faults. While the generator set is running, the display shall scroll all-important information across the screen for ease of operator use. The scroll can be stopped by pushing the rotary dial. The display shall fall asleep when the generator set is not running and will wake-up when the generator set starts or the rotary dial is depressed.

- Fault Light. The controller shall have an annunciator fault light that glows red for faults and yellow for warnings. These faults and warnings shall be displayed in the digital display. The fault light will also glow yellow when not in AUTO.

- Alarm Horn. The controller shall provide an alarm horn that sounds when any faults or warnings are present. The horn shall also sound when the controller is not in the AUTO mode.

- Alarm Silence/Lamp Test Button. When this button is depressed, it shall test all controller lamps. This button will also silence the alarm horn when the unit is not AUTO.

- USB Connection. The controller shall have a USB connection on the face of the controller. This connection shall allow for updating of all software and firmware. This port shall also allow for all servicing of generator set parameters, fault diagnostics and viewing of all controller information via use a laptop computer.

- Dedicated user inputs. The controller shall have dedicated inputs for remote emergency stop switch, remote 2-wire star for transfer switch and auxiliary shutdown.

- The controller shall have auto resettable circuit protection integral on the circuit board.

    - System Controller Monitoring and Status Features and Functions

- The generator controller shall display and monitor the following engine and alternator functions and allow adjustments of certain parameters at the controller:

- Overview menu

  - Active shutdowns and warnings shall be displayed if present and without the need of operator interface

  - Engine runtime with total hours

  - Average line to line voltage

  - Coolant temperature

  - Fuel level or pressure

  - Oil pressure

  - Battery voltage

  - Software version

  - Frequency

  - Average current

- Engine metering menu.

- Engine speed

- Oil pressure

- Coolant temperature

- Battery voltage

- Generator metering menu.

- Total power in VA

- Total power in W

- Rated power % used

- Voltage L-L and L-N for all phases

- Current L1, L2, L3

- Frequency

- Generator set information.

- Generator set model number

- Generator set serial number

- Controller set number

- Generator set run time.

- Engine run time total hours

- Engine loaded total hours

- Number of engine starts

- Total energy in kW

- Generator set system

- System voltage

- System frequency, 60Hz

- System phase, single/three phase

- Power rating kW

- Amperage rating

- Power type standby/prime

- Measurement units, metric/English units adjustable

- Alarm silence, always or auto only

- Generator set calibration, the following are adjustable at the controller.

- Voltage L-L and L-N all phases

- Current L1, L2, L3

- Reset all calibrations

- Voltage regulation, +/-0.5% regulation, the following is adjustable at the controller.

- Voltage Adjustable +/- 10%

- Digital and Analog Inputs and outputs

- Displays settings and status

- Event Log

- Stores event history, up to 1000 events

    - Controller Engine control features and functions

- Automatic restart - the controller has automatic restart feature that initiates the start routine and re-crank after a failed start attempt.

- Cyclic cranking - the controller shall have programmable cyclic cranking

- Engine starting aid - the controller shall have the capability of providing control for an optional engine starting aid.

- The control system shall include time delays for engine start and cool down.

- The control system shall interface with the engine ECM and display engine fault codes and warnings. The ECM shall also include sender failure monitoring to help distinguish between failed senders and actual failure conditions.

- The controller shall monitor and display engine governor functions with include steady state and transient frequency monitoring

    - Controller Alternator control features and functions

- Integrated hybrid voltage regulator. The system shall have integral microprocessor based voltage regulator system that provides +/- 0.5% voltage regulation, no-load to full load with three phase sensing. The system is prototype tested and control variation of voltage to frequency. The voltage regulator shall be adjustable at the controller with maximum +/- 10% adjustable of nominal voltage.

- AC output voltage regulator adjustment. The system shall allow for adjustment of the integral voltage regulator with maximum of +/- 10% adjustment of the system voltage.

- Alternator thermal overload protection. The system shall have integral alternator overload and short circuit protection matched to each alternator for the particular voltage and phase configuration.

- Power metering. The controller digitally displays power metering of kW and kVA.

    - Other control features and functions

- Event logging. The controller keeps a record of up to 1,000 events, for warning and shutdown faults. This fault information becomes a stored record of systems events and can be reset.

- Historical data logging. The controller total number of generator set successful start shall be recorded and displayed.

- Programmable access. The control system shall include a USB port that gives service technicians the ability to provide software and firmware upgrades. The system shall also be capable of allowing setting of all critical parameters using the service software and a laptop computer. All parameters and setting should be capable to being stored on a laptop for future upgrades of printing for analysis.

    - Generator Set Warning, Shutdown Alarm and Status

- The generator set shall have alarms and status indication lamps that show non-automatic status and warning and shutdown conditions. The controller shall indicate with a warning lamp and or alarm and on the digital display screen any shutdown, warning or engine fault condition that exists in the generator set system. The following alarms and shutdowns shall exist as a minimum:

  - Engine functions

- Critical high fuel level (alarm)

- ECM communication loss (shutdown)

- ECM diagnostics (alarm & shutdown)

- Engine overspeed (shutdown)

- Engine start aid active

- Engine under speed (shutdown)

- Fuel tank leak (alarm & shutdown)

- High DC battery voltage (alarm)

- High coolant temperature (alarm & shutdown)

- High fuel level (alarm)

- Low DC battery voltage (alarm)

- Low coolant level (shutdown)

- Low coolant temperature (alarm)

- Low cranking voltage (alarm)

- Low engine oil level (alarm & shutdown)

- Low fuel level (alarm & shutdown)

- Low fuel pressure (alarm)

- Low oil pressure (alarm & shutdown)

- No coolant temperature signal (shutdown)

- No oil pressure signal (shutdown)

- Overcrank (shutdown)

- Speed sensor fault (alarm)

  - Generator functions

- AC sensing loss over & under current (alarm & shutdown)

- Alternator protection (shutdown)

- Ground fault input (alarm)

- kW overload (shutdown)

- Locked rotor (shutdown)

- Over-frequency (shutdown)

- Over AC voltage (shutdown)

- Under-frequency (shutdown)

- Under AC voltage (shutdown)

- Emergency stop (shutdown)

  - Other General functions

- Battery charger fault (alarm)

- Common fault (shutdown)

- Common warning (alarm)

- Master switch not in auto (alarm)

- Generator running

- Input/Output fault (alarm)

  - The generator set controller shall also be capable of meeting all necessary NFPA 110 requirements that include several of the above along with; EPS supplying load, Master switch “not in auto”, and contacts for local and remote common alarm.

    - Communications

- If the generator set engine is equipped with an ECM (engine control module), the controller shall communicate with the ECM for control, monitoring, diagnosis, and meet SAE J1939 standards

- Kohler RBUS communication shall be available.

- RBUS shall be able to monitor and alter parameters and start or stop a generator.

- The controller shall have the capability to communicate to a personal computer (IBM or compatible) and appropriate application software

- A variety of connections shall be available based on requirements:

- A single control connection to a PC via USB

- Internet connection via Ethernet

- Generator and transfer switch controls shall be equipped with communications modules capable of connecting to the same communication network.

    - Dry Contact Kit

- The 15-relay dry contact kit shall provide normally open and normally closed contacts in a form C configuration to activate warning devices and other customer-provided accessories allowing remote monitoring of the generator set.  Typically, lamps, audible alarms, or other devices signal faults or status conditions

  - Customer connection panel

Viewable generator set controller with security cover.

Remote start/stop terminal connections.

Shore Power circuit breaker protected GFCI receptacle, rated at 120V, 15 amp, for on-site power for the battery charger plus battery heater.

Shore Power circuit breaker protected GFCI receptacle, rated at 120V, 15 amp, for on-site power for the block heater.

Two convenience circuit breakers protected GFCI receptacles, rated at 120V, 15 amp, for customer use.

Three convenience circuit breakers protected GFCI receptacles, rated at 240V, 50 amp, twistlock type for customer use.

Load lug connections, one per phase plus ground and neutral, #6-350MCM, 400 amp load lugs located behind lockable controller door and secondary panel.

Color-coded camlock connectors.

Externally mounted, recessed emergency stop switch.

  - Generator Overcurrent and Fault Protection

Adjustable trip main line 400 amp circuit breaker

  - Alternator

    - The alternator shall be salient-pole, brushless, 2/3-pitch, with 4 bus bar provision for external connections, self-ventilated, with drip-proof construction and amortisseur rotor windings, and skewed for smooth voltage waveform. The ratings shall meet the NEMA standard (MG1-32.40) temperature rise limits. The insulation shall be class H per UL 1446 and the varnish shall be a fungus resistant epoxy. Temperature rise of the rotor and stator shall be limited to 150°C Standby. The PMG based excitation system shall be of brushless construction controlled by a digital, solid- state, voltage regulator. The AVR shall be capable of proper operation under severe nonlinear loads and provide individual adjustments for voltage range, stability and volts-per-hertz operations. The AVR shall be protected from the environment by potting compound. The waveform harmonic distortion shall not exceed 5% total RMS measured line-to-line at full rated load. The TIF factor shall not exceed 50.

    - The alternator shall have a maintenance-free bearing, designed for 40,000-hour B10 life. The alternator shall be directly connected to the flywheel housing with a semi-flexible coupling between the rotor and the flywheel.

    - The generator shall be inherently capable of sustaining at least 300% of rated current for at least 10 seconds under a 3-phase symmetrical short circuit without the addition of separate current-support devices.

    - Motor starting performance and voltage dip determinations shall be based on the complete generator set.  The generator set shall be capable of supplying 448.00 LRKVA for starting motor loads with a maximum instantaneous voltage dip of 35%, as measured by a digital RMS transient recorder in accordance with IEEE Standard 115.  Motor starting performance and voltage dip determination that does not account for all components affecting total voltage dip, i.e., engine, alternator, voltage regulator, and governor will not be acceptable.  As such, the generator set shall be prototype tested to optimize and determine performance as a generator set system.

  - Vibration Isolation

    - Vibration isolators shall be provided between the engine-alternator and heavy-duty steel base.

- Accessories

Two-Way Fuel Valve – The two-way fuel valve and fuel line connection ports will allow switching between on-board fuel and external fuel sources.

Cold weather package - A block heater, battery heater pad and a battery wrap are included in the kit.  The kit improves starting performance in cold weather conditions.

The generator set shall be supplied with a 6-ampere automatic float/equalize battery charger capable of charging both lead-acid and gel-cell type batteries, with the following features:

  - Automatic 3-stage float to equalization charge

  - 1% steady-state voltage regulation from no load to full load over 10% AC input line voltage variation

  - Indicator LED lamps for charge state indication (bulk charge/absorption/float)

  - Ambient temperature operating range: -40°C to 70°C

  - Potting for durability and waterproofing

  - Short-circuit and reverse polarity protection

  - UL 1236 listed

  - UL 2200 compliant

  - CSA certified

  - Ring terminals for battery connection.

- Source Quality Control

  - Non-Conforming Work

    - To ensure that the equipment has been designed and built to the highest reliability and quality standards, the manufacturer and/or local representative shall be responsible for three separate tests: design prototype tests, final production tests, and site tests.

- Design Prototype Tests. Components of the emergency system, such as the engine/generator set, transfer switch, and accessories, shall not be subjected to prototype tests because the tests are potentially damaging.  Rather, similar design prototypes and preproduction models shall be subject to the following tests:

- Maximum power (kW)

- Maximum motor starting (kVA) at 35% instantaneous voltage dip.

- Alternator temperature rise by embedded thermocouple and/or by resistance method per NEMA MG1-32.6.

- Governor speed regulation under steady-state and transient conditions.

- Voltage regulation and generator transient response.

- Harmonic analysis, voltage waveform deviation, and telephone influence factor.

- Three-phase short circuit tests.

- Alternator cooling air flow.

- Torsional analysis to verify that the generator set is free of harmful torsional stresses.

- Endurance testing.

- Final Production Tests. Each generator set shall be tested under varying loads with guards and exhaust system in place.  Tests shall include:

- Single-step load pickup

- Safety shutdown device testing

- Rated Power @ 0.8 PF

- Maximum power

- Upon request, a witness test, or a certified test record sent prior to shipment.

- Site Tests. The manufacturer's distribution representative shall perform an equipment check, startup, and building load test. The engineer, regular operators, and the maintenance staff shall be notified of the time and date of the site test. The tests shall include:

- Fuel, lubricating oil, and antifreeze shall be checked for conformity to the manufacturer's recommendations, under the environmental conditions present and expected.

- Accessories that normally function while the set is standing by shall be checked prior to cranking the engine.  These shall include: block heaters, battery chargers, alternator strip heaters, remote annunciators, etc. if equipped.

- Generator set startup under test mode to check for path of exhaust gases near the building, movement during starting and stopping, vibration during operation, normal and emergency line-to-line voltage and frequency, and phase rotation.

- Automatic start by means of a simulated power outage to test remote-automatic starting, transfer of the load, and automatic shutdown.  Prior to this test, all transfer switch timers shall be adjusted for proper system coordination.  Engine coolant temperature, oil pressure, and battery charge level along with generator set voltage, amperes, and frequency shall be monitored throughout the test.

END OF SECTION