SECTION 263213.13 - DIESEL-ENGINE-DRIVEN GENERATOR SETS

Copyright 2022 Kohler Co.  This document is a modification and derivative work of a Masterspec based document licensed to Kohler by Deltek

To view non-printing Editor's Notes (visible in blue font) that provide guidance for editing, click on the ¶ symbol in the paragraph section under the Home menu.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Engine-generator assembly.

          - Diesel engine.

          - Diesel fuel-oil system.

          - Control and monitoring.

          - Generator overcurrent and fault protection.

          - Generator paralleling.

          - Alternator, exciter, and voltage regulator.

          - Load bank.

          - Outdoor engine generator enclosure.

          - Remote radiator motors.

          - Vibration isolation devices.

          - Finishes.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 262313 "Paralleling Low-Voltage Switchgear" for controls and paralleling equipment for large or multiple parallel engine generators.

          - Section 263600 "Transfer Switches" for transfer switches including sensors and relays to initiate automatic-starting and -stopping signals for engine generators.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

If using Section 260800 "Commissioning of Electrical Systems," coordinate use of the terms "emergency" and "essential."

        - ECM: Engine control module.

        - EPS: Emergency power supply.

        - EPSS: Emergency power supply system.

        - Operational Bandwidth: The total variation from the lowest to highest value of a parameter over the range of conditions indicated, expressed as a percentage of the nominal value of the parameter.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

          - Include thermal damage curve for generator.

          - Include time-current characteristic curves for generator protective device.

          - Include fuel consumption in gallons per hour (liters per hour) at 0.8 power factor at 50, 75, and 100 percent of generator capacity.

          - Include generator efficiency at 0.8 power factor at 0.5, 0.75, and 1.0 times generator capacity.

          - Include airflow requirements for cooling and combustion air in cubic feet per minute (cubic meters per minute) at 0.8 power factor at [104 deg F (40 deg C)] [122 deg F (50 deg C)] cooling system rating. Provide radiator air flow restriction data for ambient rating.

          - Include generator characteristics, including, but not limited to, kilowatt rating, efficiency, reactances, and short-circuit current capability.

        - Shop Drawings:

          - Include plans and elevations for engine generator and other components specified. Indicate access requirements affected by height of subbase fuel tank.

          - Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Identify fluid drain ports.

          - Vibration Isolation Base Details: Detail including anchorages and attachments to structure and to supported equipment. Include base weights.

          - Include diagrams for power, signal, and control wiring. Complete schematic, wiring, and interconnection diagrams showing terminal markings for engine generators and functional relationship between all electrical components.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [Installer] [manufacturer] [and] [testing agency].

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: Certificates, for engine generator, accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: With engine and generator mounted on rails, identify center of gravity and total weight [, including], [supplied enclosure,] [silencer,] [subbase-mounted fuel tank,] and each piece of equipment not integral to the engine generator, and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate "Source Quality-Control Reports" Paragraph below with "Source Quality Control" Article.

        - Source Quality-Control Reports: Including, but not limited to, the following:

          - Certified Summary of prototype-unit test report.

          - Certified Test Reports: For components and accessories that are equivalent, but not identical, to those tested on prototype unit.

          - Report of factory test on units to be shipped for this Project, showing evidence of compliance with specified requirements.

          - Report of sound generation.

          - Report of exhaust emissions showing compliance with applicable regulations.

Requirement below is from Section 5.6.10.2 of NPFA 110.

          - Certified Torsional Vibration Compatibility: Comply with NFPA 110.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For packaged engine generators to include in emergency, operation, and maintenance manuals.

          - In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

            - List of tools and replacement items recommended to be stored at Project for ready access. Include part and drawing numbers, current unit prices, and source of supply.

            - Training plan.

      - MAINTENANCE MATERIAL SUBMITTALS

Extra materials may not be allowed for publicly funded projects.

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Quantities below are examples only.

          - Fuses: One for every 10 of each type and rating, but no fewer than one of each.

          - Replaceable Indicator Lamps: Two for every six of each type used, but no fewer than two of each.

          - Filters: One set each of lubricating oil, fuel, and combustion-air filters.

          - Tools: Each tool listed by part number in operations and maintenance manual.

      - QUALITY ASSURANCE

        - Manufacturer Qualifications:

          - ISO 9001 certified for design, development, production and service complete product line.

          - Produced this type of equipment for a period of at least 10 years.

          - Actively maintaining a 24-hour parts and service organization regularly engaged in maintenance contract programs to perform preventive maintenance and service on equipment similar to that specified.

          - Furnish a service agreement that includes system operation under simulated operating conditions; adjustment to the generator set, transfer switch, and switchgear controls as required, and certification in the owner's maintenance log of repairs made and functional tests performed on all systems.

          - Engine-driven generator assembly furnished by a single manufacturer, responsible for design, coordination, and testing of the complete system.

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency. in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements."

        - Testing Agency Qualifications: Accredited by NETA.

          - Testing Agency's Field Supervisor: Certified by NETA to supervise on-site testing.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Manufacturer's Warranty: Manufacturer agrees to repair or replace components of packaged engine generators and associated auxiliary components that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components. Typical manufacturer's warranty for a prime rated unit is one year. Two- and five-year warranties and normal and extended manufacturer warranties may be available at additional cost.

          - Warranty Period: <Insert number> years from date of registered startup or commissioning.

          - The generator set to include a standard warranty covering one (1) years or 2000 hours standby, whichever occurs first (hours or years), to warrant against defective material and workmanship in accordance with the manufacturer's published warranty from the date of initial startup.

          - Extended limited warranties that can be obtained include: Stationary Standby two (2) year or 2000 hour, Stationary Standby five (5) year or 3000 hours, Stationary Standby five (5) year or 3000 hours comprehensive.

- PRODUCTS

      - MANUFACTURERS

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Kohler Power Systems strongly recommends the use of a generator sizing program like "Power Solutions Center" available here: https://kohlerpower.com/en/generators/industrial/sizing-program to ensure the selection of the optimum engine and generator combination for your Project.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Kohler Power Systems; REOZJ Series engine generator offerings or comparable product by one of the following:

          - Caterpillar, Inc.; Electric Power Division.

          - Cummins Power Generation.

        - Source Limitations: Obtain packaged engine generators and auxiliary components from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Data" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Engine generator housing, [subbase fuel tank,] [day tank,] engine generator, batteries, battery racks, silencers, sound attenuating equipment, accessories, and components to withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>.

          - The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified [ and the unit will be fully operational after the seismic event]."

          - Shake-table testing to comply with ICC-ES AC156. Testing to be performed with all fluids at worst-case normal levels. [ Water to be substituted for diesel fuel in fuel tank during test.]

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

        - B11 Compliance: Comply with B11.19.

        - NFPA Compliance:

          - Comply with NFPA 30.

          - Comply with NFPA 37.

          - Comply with NFPA 70.

Retain first subparagraph below for healthcare facilities.

          - Comply with NFPA 99.

Retain subparagraph below for projects requiring NFPA 110 compliance.

          - Comply with NFPA 110 requirements for Level [1] [2] EPSS.

        - UL Compliance: Comply with UL 2200 "Stationary Engine Generator Assemblies."

        - CSA Compliance: Comply with CSA.

        - Engine Exhaust Emissions: Comply with EPA Tier 3 requirements and applicable state and local government requirements.

Retain "Noise Emission" Paragraph below for installations with noise-abatement requirements. Coordinate with noise-reduction features in the design, including cooling-air intake and discharge arrangement, muffler specification and location and orientation as indicated on Drawings.

        - Noise Emission: Comply with <Insert Project criteria> for acceptable noise level at [adjacent property boundaries] <Insert critical locations>.

Retain the subparagraph below for indoor installations. Refer to manufacturer's test data for the model being specified.

          - Maximum exhaust isolated sound pressure emitted by engine generator 93.8 dBA at a distance of 23 ft. (7 m) while operating at 100 percent load and including engine, engine exhaust, engine cooling-air intake and discharge, and other components of installation.

Retain the subparagraph below for outdoor installations. Refer to manufacturer's test data for the model being specified. Note that specifying a maximum sound pressure value lower than listed will likely require a custom-designed enclosure at increased cost.

          - Maximum sound pressure emitted by engine generator within sound-attenuating enclosure of [91] [83] [75] <insert number> dB(A) at a distance of 23 ft. (7 m) while operating at 100 percent load and including engine, engine exhaust, engine cooling-air intake and discharge, and other components of installation.

        - Environmental Conditions: Engine generator system to withstand the following environmental conditions without mechanical or electrical damage or degradation of performance capability:

Retain "Ambient Temperature" Subparagraph below if engine generator is installed outdoors. Consult engine generator manufacturer de-rate tables or use sizing software program to estimate performance at site conditions. Coordinate with Drawings.

          - Ambient Temperature: 5 deg F (Minus 15 deg C) to [77 deg F (25 deg C)] <Insert temperature>.

          - Altitude: Sea level to [984 ft. (300 m)] <Insert altitude>.

      - ENGINE GENERATOR ASSEMBLY DESCRIPTION

        - Factory-assembled and -tested, liquid-cooled engine, with brushless generator and accessories.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and use.

        - Power Rating: [Standby] [Prime].

"Overload Capacity" Paragraph below is only applicable if retaining "prime" option in "Power Rating" Paragraph above.

        - Overload Capacity: 110 percent of service load for 1 hour in 12 consecutive hours.

Retain "EPSS Class" Paragraph below if retaining "standby" option in "Power Rating" Paragraph above. "Class," as used in "EPSS Class" Paragraph below, refers to the number of hours the EPSS is required to operate at full load without refueling. Coordinate with seismic design criteria. NFPA 110 requires seismic Categories C, D, E, and F to have a minimum 96-hour fuel supply for Level 1 engine generators.

        - EPSS Class: Engine generator to be classified as a [Class 2] [Class 6] [Class 24] [Class 48] [Class 96] <Insert classification> in accordance with NFPA 110.

Retain "Tank Capacity Run Hours" for installations not classified as EPSS by NFPA 110. Note that not all tank sizes are available in all engine-generator models, verify capacity with manufacturer.

        - Tank Capacity Run Hours: [12] [24] [48] [72] [96] <insert number> hours.

        - Nameplate Rating: 400 kW.

        - Power Factor: 0.8, lagging.

        - Frequency: 60 Hz.

        - Voltage: [208] [240] [480] [600] <insert number>-V ac.

        - Phase: Three-phase, four-wire, wye.

        - Governor: Adjustable isochronous, with speed sensing.

        - Mounting Frame: Structural steel framework to maintain alignment of mounted components without depending on concrete foundation. Provide lifting attachments sized and spaced to prevent deflection of base during lifting and moving.

Coordinate "Capacities and Characteristics" Paragraph below with prototype test requirements in "Informational Submittals" and "Source Quality Control" articles.

        - Capacities and Characteristics:

          - Power Output Ratings: Nominal ratings as indicated at 0.8 power factor excluding power required for the continued and repeated operation of the unit and auxiliaries [, with capacity as required to operate as a unit as evidenced by records of prototype testing].

          - Nameplates: For each major system component to identify manufacturer's name and address, and model and serial number of component.

Retain one of the two following paragraphs below. Retain "Engine Generator Performance" Paragraph below for loads involving little or no sensitive electronic equipment or adjustable frequency drives.

        - Engine Generator Performance:

          - Steady-State Voltage Operational Bandwidth: 0.5 percent of rated output voltage from no load to full load.

          - Transient Voltage Performance: Not more than 20 percent variation for 50 percent step-load increase or decrease and meets ISO8528-5, Class G2 for standard loads. Voltage to recover and remain within the steady-state operating band within six seconds.

          - Steady-State Frequency Operational Bandwidth: 0.25 percent of rated frequency from no load to full load.

          - Transient Frequency Performance: Less than 10 percent variation for 50 percent step-load increase or decrease and meets ISO8528-5, Class G2 for standard loads. Frequency to recover and remain within the steady-state operating band within five seconds.

          - Output Waveform: At no load, harmonic content measured line to line or line to neutral may not exceed 5 percent total and 3 percent for single harmonics. Telephone influence factor, determined in accordance with NEMA MG 1, may not exceed 50.

          - Sustained Short-Circuit Current: For a three-phase, bolted short circuit at system output terminals, system to supply a minimum of 250 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to generator system components.

          - Start Time:

Retain subparagraph below for standby generators that require start time within 10 seconds under specific conditions and includes startup only, not load assumption.

            - Comply with NFPA 110, Type 10 system requirements.

Retain "Engine Generator Performance for Sensitive Loads" Paragraph below for loads involving sensitive electronic equipment or significant (25 percent or more) nonlinear load elements.

        - Engine Generator Performance for Sensitive Loads:

          - Oversizing generator compared with the rated power output of the engine is permissible to meet specified performance.

            - Nameplate Data for Oversized Generator: Show ratings required by the Contract Documents rather than ratings that would normally be applied to generator size installed.

Some manufacturers may be required to provide an oversized engine generator to meet parameters in "Steady-State Voltage Operational Bandwidth" Subparagraph below. Oversizing an engine generator could impact space, noise, ventilation, cooling, cost, and other parameters. Verify performance of products if specific manufacturers are listed. Revise requirements below to suit actual Project load characteristics.

          - Steady-State Voltage Operational Bandwidth: 0.5 percent of rated output voltage from no load to full load.

          - Transient Voltage Performance: Not more than 15 percent variation for 50 percent step-load increase or decrease and meets ISO8528-5, Class G3 for sensitive loads. Voltage to recover and remain within the steady-state operating band within four seconds.

          - Steady-State Frequency Operational Bandwidth: Plus or minus 0.25 percent of rated frequency from no load to full load.

          - Transient Frequency Performance: Less than 7 percent variation for 50 percent step-load increase or decrease and meets ISO8528-5, Class G3 for sensitive loads. Frequency to recover and remain within the steady-state operating band within three seconds.

          - Output Waveform: At no load, harmonic content measured line to line and line to neutral may not exceed 5 percent total or 3 percent for a single harmonic. Telephone influence factor, determined in accordance with NEMA MG 1, may not exceed 50.

          - Sustained Short-Circuit Current: For a three-phase, bolted short circuit at system output terminals, system to supply a minimum of 300 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to winding insulation or other generator system components.

          - Excitation System: Performance to be unaffected by voltage distortion caused by nonlinear load.

          - Start Time:

Retain subparagraph below for standby generators that requires start time within 10 seconds under specific conditions and includes startup only, not load assumption.

            - Comply with NFPA 110, Type 10 system requirements.

      - DIESEL ENGINE

        - Fuel: ASTM D975, [diesel fuel oil, Grade 2-D S15] [hydrotreated vegetable oil/ renewable diesel].

        - Rated Engine Speed: 1800 rpm.

        - Minimum Standby Load Factor Rating: 70 percent.

        - Lubrication System: Engine or skid-mounted.

          - Filter and Strainer: Rated to particles that may damage engine per manufacturer's written instructions while passing full flow.

          - Thermostatic Control Valve: Control flow in system to maintain optimum oil temperature. Unit to be capable of full flow and is designed to be fail-safe.

          - Closed Crankcase Ventilation: System: Prevents crankcase oil vapor from draining or escaping the engine.

          - Crankcase Drain: Arranged for complete gravity drainage to an easily removable container with no disassembly and without use of pumps, siphons, special tools, or appliances.

"Jacket Coolant Heater" Paragraph below is an optional feature, often used on emergency generators, where required by NFPA 110 5.3.1, to keep engine jacket-water temperature within certain parameters. Coordinate with Drawings for electrical supply.

        - Jacket Coolant Heater: Electric-tank type, factory installed in coolant jacket system. Comply with UL 499[ and with NFPA 110 requirements for Level 1 equipment for heater capacity].

Retain "Integral Cooling System" or "Remote Cooling System" Paragraph below. Coordinate with Drawings. Review manufacturer’s options for generator-mounted cooling system. Some models use charge air cooling.

        - Integral Cooling System: Closed loop, liquid cooled, with radiator factory mounted on engine generator set mounting frame and integral engine-driven coolant pump.

          - Coolant: Solution of 50 percent ethylene-glycol-based antifreeze and 50 percent water, with anticorrosion additives as recommended by engine manufacturer.

          - Size of Radiator: Adequate to contain expansion of total system coolant to 110 percent of capacity.

          - Expansion Tank: Constructed of welded steel plate and rated to withstand maximum closed-loop coolant system pressure for engine used. Equip with gage glass and petcock.

          - Temperature Control: Self-contained, thermostatic-control valve modulates coolant flow automatically to maintain optimum constant coolant temperature as recommended by engine manufacturer.

          - Coolant Hose: Flexible assembly with inside surface of nonporous rubber and outer covering of aging-, UV-, and abrasion-resistant material.

            - Rating: 50-psig (345-kPa) maximum working pressure with coolant at 215 deg F (102 deg C), and noncollapsible under vacuum.

Retain first option in "Remote Cooling System" Paragraph below for remote radiator cooling unless friction head is exceeded. If both static and friction heads are exceeded, a heat exchanger cooling system may be required. Coordinate with engine generator manufacturer for remote radiator or heat exchanger cooling. Indicate remote radiator location on Drawings.

        - Remote Cooling System: Closed loop, liquid cooled, with remote radiator and [integral engine driven] [auxiliary] coolant pump. Comply with requirements in Section 232113 "Hydronic Piping" for coolant piping.

          - Configuration: [Vertical] [Horizontal] air discharge.

          - Radiator Core Tubes: [Aluminum] [Nonferrous-metal construction other than aluminum].

See Section 077200 "Roof Accessories" for the type and style of roof curbs and equipment supports for a remote radiator mounted on the roof.

          - Size of Radiator: Adequate to contain expansion of total system coolant to 110 percent of capacity.

          - Expansion Tank: Constructed of welded steel plate and rated to withstand maximum closed-loop coolant system pressure for engine used. Equip with gauge glass and petcock.

          - Vent and Balance Lines: Provisions must be available between engine and radiator.

          - Fan: Driven by totally enclosed electric motor with sealed bearings.

          - Coolant: Solution of 50 percent ethylene-glycol-based antifreeze and 50 percent water, with anticorrosion additives as recommended by engine manufacturer.

          - Temperature Control: Self-contained, thermostatic-control valve modulates coolant flow automatically to maintain optimum constant coolant temperature as recommended by engine manufacturer.

        - Muffler/Silencer:

Retain this Article only for open units (typically installed within a building).

Retain one of two subparagraphs below. Revise dBA requirements to accommodate environment in which engine generator is operating. If unit is specified with an enclosure, consider specifying sound level requirements at specified distance.

          - Critical type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

            - Minimum sound attenuation of 25 dB at 500 Hz.

Retain second option in "Air-Intake Filter" Paragraph below if filters may not be serviced as often as recommended. If air contaminant level is excessive, consult manufacturers to determine if special filtration of combustion air is needed.

        - Air-Intake Filter: [Standard] [Heavy]-duty, engine-mounted air cleaner with replaceable dry-filter element and "blocked filter" indicator.

        - Starting System: 24-V dc electric, with negative ground.

Retain first option in "Cranking Cycle" Subparagraph below if "Performance Requirements" Article specifies NFPA 110, Level 1 or 2; otherwise, retain second.

          - Cranking Cycle: [As required by NFPA 110 for system level specified] [60 seconds].

Lead-acid batteries are less expensive and perform as well or better than nickel cadmium if temperatures are maintained between 0 and 100 deg F (minus 18 and plus 38 deg C). Note that valve-regulated lead-acid batteries are even more subject to thermal stresses and are not recommended for engine generator starting service. AGM batteries provide increased durability and require less maintenance compared to standard lead-acid batteries. Nickel-cadmium batteries have better characteristics in more extreme temperature applications. Verify requirements for eyewash in the vicinity of the batteries with authorities having jurisdiction. Two cranking cycles complies with NFPA 110 requirements. Three cranking cycles is a more conservative rule used for some industrial applications.

          - Battery: [Lead acid] [AGM maintenance free] [Nickel cadmium], with capacity within ambient temperature range specified in "Performance Requirements" Article to provide specified cranking cycle at least [twice] [three times] without recharging.

Coordinate "Battery Cable" Subparagraph below with Drawings.

          - Battery Cable: Size as recommended by engine manufacturer for cable length indicated. Include required interconnecting conductors and connection accessories.

Retain "Battery Heater" Subparagraph below if required.

          - Battery Heater: Thermostatically controlled heater to be arranged to maintain battery above 50 deg F (10 deg C) regardless of external ambient temperature within range specified in "Performance Requirements" Article. Include accessories required to support and fasten batteries in place. Provide ventilation to exhaust battery gases.

          - Battery-Charging Alternator: Factory mounted on engine with solid-state voltage regulation and continuous rating per manufacturer's standard.

        - Battery Charger:

          - Source Limitations: Obtain battery charger from engine-driven generator manufacturer.

          - UL Compliance: Comply with UL 1236 for Category BBHH.

          - CE Certified.

          - NFPA Compliance: Comply with NFPA 110.

          - Environmental Conditions: Battery charger to withstand the following environmental conditions without mechanical or electrical damage or degradation of performance capability:

            - Ambient Temperature: Minus 40 to plus 185 deg F (Minus 40 to plus 85 deg C) with full charger output available up to 122 deg F (50 deg C).

            - Relative Humidity: 0 to 95 percent.

            - Altitude: Meets full performance requirements from sea level to 5000 ft. (1600 m). Chargers installed at higher altitudes may automatically derate output power to prevent overheating of internal components but remain operable.

          - Charger Operation: Current-limited, constant-voltage, automatic-boost-type charger designed for [lead-acid] [AGM maintenance-free] [nickel-cadmium] batteries, with the following features:

            - Automatic three-stage charge cycle for up to three independent batteries simultaneously per charger.

            - Output Voltage Regulation: Charger regulates output to within plus or minus 0.5 percent of manufacturer-provided voltage settings despite variations of input voltage, input frequency, and output current.

            - Battery Thermal Compensation: Battery temperature compensation with adjustable slope, factory set at minus 0.18 percent per degree C, and equipped for sensing battery temperature. [ Include battery temperature sensor mounted on battery negative terminal.]

            - AC Input: Charger operates from any 45- to 65-Hz ac source with voltage ranging from 105- to 264-V rms.

Retain "LCD Digital Display" Subparagraph below for NFPA level 1 installations.

          - LCD Digital Display: AC input voltmeter, DC output voltmeter, and ammeter (1 percent accuracy).

          - LED Lamp Indicators: Current limit, AC ON, and charger fail.

          - Charger Fail Alarm Contact: Voltage-free (dry type) form "C" output.

          - Filtered output for type VRLA AGM batteries.

          - Charger Enclosure: NEMA 250, Type 1 (IP20), wall mounted and rated for generator duty with charger enclosure vibration resistance.

      - DIESEL FUEL-OIL SYSTEM

        - Piping: Fuel-oil piping to be Schedule 40 black steel, complying with requirements in Section 231113 "Facility Fuel-Oil Piping." Cast iron, aluminum, copper, and galvanized steel may not be used in the fuel-oil system.

        - Main Fuel Pump: Mounted on engine to provide primary fuel flow under starting and load conditions.

        - Fuel Filtering: Remove water and contaminants larger than 1 micron.

        - Relief-Bypass Valve: Automatically regulates pressure in fuel line and returns excess fuel to source.

Retain one or more of three types of fuel tank specified below.

Large subbase tanks can raise the generator, making maintenance access difficult; subbase tanks are also of limited capacity, making them generally unsuitable for prime power applications. Design for access platform or other methods of maintenance access. Coordinate platform with room size, seismic qualification, stair requirements, height restrictions, and structural capacity. Note that handrails may be required depending on height above finished floor. Handrails may need to be removable for some maintenance activities.

        - Subbase-Mounted, Double-Wall, Fuel-Oil Tank: Complying with UL 142 and including the following features:

Consult tank manufacturers about capacities available for size of set in Project.

          - Steel Channel Support System: Reinforced steel box channel for generator support. Full height gussets at either end of channel and at generator mounting locations.

          - Fuel Level Gauge: Direct-reading, UL-listed, magnetic fuel level gauge with a hermetically sealed, vacuum-tested dial.

          - Low-Fuel Alarm Contact: Float-type switch for remote or local annunciation of a low-fuel-level condition.

          - Fill Tube: 2-inch (25-mm) NPT opening with lockable cap.

          - Leak detection in interstitial space.

          - Vandal-resistant fill cap.

          - Fill-pipe spill containment, minimum capacity 5 gal. (19 L).

          - Emergency inner- and outer-tank UL-listed relief vents sized in accordance with American Petroleum Institute Standard No 2000 with an opening pressure of 0.5 psig (3.5 kPa) and full opening pressure of 2.5 psig (17 kPa).

Determine applicable codes and regulations, and coordinate "Containment Provisions" Subparagraph below with Drawings.

          - Containment Provisions: Comply with requirements of authorities having jurisdiction.

        - Day Tank: Comply with UL 142, freestanding, factory-fabricated fuel tank assembly, with integral, float-controlled transfer pump and the following features:

          - Containment: Integral rupture basin with a capacity of 150 percent of nominal capacity of day tank.

            - Leak Detector: Locate in rupture basin and connect to provide audible and visual alarm in the event of day-tank leak.

Revise hours in "Tank Capacity" Subparagraph below or delete subparagraph and indicate capacity on Drawings. Coordinate with Drawings and NFPA 110 requirements.

          - Tank Capacity: [As recommended by engine manufacturer for an uninterrupted period of two hours' operation at 100 percent of rated power output of engine generator system without being refilled] <Insert gallons (liters)>.

          - Pump Capacity: Exceeds maximum flow of fuel drawn by engine-mounted fuel supply pump at rated capacity, including fuel returned from engine.

          - Low-Level Alarm Sensor: Liquid-level device operates alarm contacts at 85 percent of normal fuel level.

Revise "High-Level Alarm Sensor" Subparagraph below or delete if not required. Coordinate with "Control and Monitoring" Article.

          - High-Level Alarm Sensor: Liquid-level device operates alarm and redundant fuel shutoff contacts at midpoint between overflow level and 100 percent of normal fuel level.

          - Piping Connections: Factory-installed fuel supply and return lines from tank to engine; local fuel fill, vent line, overflow line; and tank drain line with shutoff valve.

"Redundant High-Level Fuel Shutoff" Subparagraph below describes an optional feature. Note that this feature is not allowed on a Level 1 EPSS per NFPA 110.

          - Redundant High-Level Fuel Shutoff: Actuated by high-level alarm sensor in day tank to operate a separate motor-control device that disconnects day-tank pump motor. Sensor signals solenoid valve, located in fuel suction line between fuel storage tank and day tank, to close. Both actions remain in shutoff state until manually reset. Shutoff action initiates an alarm signal to control panel but does not shut down engine generator.

        - Fuel-Oil Storage Tank: Comply with requirements in [Section 231313 "Facility Underground Fuel-Oil Storage Tanks."] [Section 231323 "Facility Aboveground Fuel-Oil Storage Tanks."]

Consult tank manufacturers about capacities available for size of set in Project.

          - Fuel Tank Capacity: <Insert gallons (liters)>.

          - Duplex Fuel-Oil Transfer Pump: Comply with requirements in Section 231213 "Facility Fuel-Oil Pumps."

      - CONTROL AND MONITORING

This article specifies the subsystem that monitors, protects, and controls the engine generator.

        - Automatic Starting System Sequence of Operation: When mode-selector switch on the control and monitoring panel is in the automatic position, remote-control contacts in one or more separate automatic transfer switches initiate starting and stopping of engine generator. When mode-selector switch is switched to the on position, engine generator starts. The off position of the same switch initiates generator-set shutdown. When the engine generator is running, specified system or equipment failures or derangements automatically shut down engine generator and initiate alarms.

Kohler APM603 controller complies with UL 6200 while the APM402 controller complies with UL 508A.

        - Comply with [UL 508A] [UL 6200].

        - Configuration:

          - Operating and safety indications, protective devices, basic system controls, and engine gauges will be grouped in a common control and monitoring panel mounted on the engine generator. The mounting method will isolate the control panel from generator-set vibration. Panel will be powered from the engine generator battery.

        - Control and Monitoring Panel:

Retain one of first two subparagraphs below. First subparagraph is for the Kohler APM603 controller; second is for the Kohler APM402 controller.

          - Digital engine generator controller with integrated 7-inch (175-mm) graphical touch screen TFT display and microprocessor, capable of local and remote control, monitoring, and programming, with battery backup.

          - Digital engine generator controller with integrated alphanumeric display, providing two lines of data. The display has back lighting for ease of operator use in high- and low-light conditions. Capable of local and remote control, monitoring, and programming.

Retain first subparagraph below for the Kohler APM603 controller.

          - Controller Face Ingress Protection: IP 65.

          - Operating Temperature: Minus 40 to plus 158 deg F (Minus 40 to plus 70 deg C).

          - Maximum Operating Humidity: 95 percent noncondensing.

          - Corrosion Resistant: Tested in accordance with ASTM B117 (salt spray test).

          - Controller Features:

            - Mode Selector: Allowing selection of one of the following modes:

              - Off/Reset: Prohibits the generator from starting and resets shutdowns. In this mode, the controller does not respond to remote start and stop commands.

              - Manual: Allows user to locally start and stop to operate the generator. In this mode, the controller does not respond to remote start and stop commands.

              - Auto: Allows generator to start and stop based on remote commands. In this mode, the generator does not respond to manual start and stop commands.

            - Emergency Stop Switch: Latch-type remote stop switch, red in color with mushroom-type head. Depressing the stop button will immediately stop the generator set and lock out any automatic remote starting.

            - Audible Alarm: Horn sounds for specific warning and shutdown conditions.

            - Alarm Silence/Lamp Test Pushbutton: Silences audible alarm when depressed. All controller-indicating lights are simultaneously illuminated while actuated.

            - Fault Light: LED indicating abnormal conditions:

              - Yellow: Active warning condition or mode selector switch not in automatic.

              - Red: Active shutdown condition.

Retain first subparagraph below for Kohler APM603 controller.

            - Real-time clock and calendar for time-stamping events.

Retain "Load Management" Subparagraph below if required. Only the Kohler APM603 controller includes this functionality.

            - Load Management:

              - Programmable outputs to command the connect and disconnect of loads based on system state:

                - Loads connected based on available capacity.

                - Loads disconnected at system startup.

                - Loads disconnected based on a maximum kW setting or underfrequency setting.

              - Support up to 16 load steps.

            - Engine Control Features:

              - Programmable engine start delay.

              - Programmable engine cool-down delay.

              - Programmable warm-up delay based on time or engine temperature.

              - Programmable idle speed.

              - Programmable cyclic cranking with adjustable on time, off time, and number of cycles.

            - Event Logging:

              - Maintain record of a minimum of 1,000 events with date and time locally for warning and shutdown faults.

Retain first two subparagraphs below for the Kohler APM603 controller.

              - Event log easily available for download onto USB storage device or PC.

              - Event Snapshot: Capture 15 seconds of critical data around the time of a fault or warning. Data to be viewable on the controller and downloadable.

Retain first four subparagraphs below for the Kohler APM603 controller.

            - Data Logging: Capable of time-based recording of customized parameters.

              - Parameters selectable from all monitored parameters.

              - Sample period configurable from one second to one day.

              - Collected data stored on USB storage device plugged into the control panel.

            - Minimum of three user access levels.

            - Password protection to prevent unauthorized modification to system parameters.

            - Customizable Interface:

Retain first two subparagraphs below for the Kohler APM603 controller.

              - Overview Screen: Dedicated screen allowing user to display up to 16 parameters for immediate access.

              - Favorites: User-customizable menu set up for enhanced usability.

          - Monitoring Instruments: Accessible through the digital engine generator controller and viewable during operation.

            - Engine-coolant temperature.

            - Battery voltage.

            - Running-time meter.

            - Engine speed.

            - Oil pressure.

            - Fuel level (with optional sensor)

            - Fuel pressure.

Retain first three subparagraphs below for the KPS APM603 controller.

            - Fuel Consumption.

            - Exhaust temperature (with optional sensor).

            - Ambient temperature.

Retain first two subparagraphs below if a charge air cooling system is required, which is only available with Kohler APM603 controller.

            - Charge air pressure.

            - Charge air temperature.

First three subparagraphs below are required for Level 1 engines by NFPA 110, Article 5.6.9.9. Retain 0.25 percent accuracy for Kohler APM603 or 0.5 percent accuracy for Kohler APM402 controller.

            - AC output voltage for each phase, [0.25] [0.5] percent accuracy.

            - AC output current for each phase, [0.25] [0.5] percent accuracy.

            - AC frequency meter, [0.25] [0.5] percent accuracy.

Retain first subparagraph below for the Kohler APM603 controller.

            - Power factor total and per phase with leading/lagging indication.

In first three subparagraphs below, retain 0.5 percent accuracy for Kohler APM603 or 1 percent accuracy for Kohler APM402 controller.

            - kW total and per phase, [0.5][1] percent accuracy.

            - kVARS total and per phase, [0.5][1] percent accuracy.

            - kVA total and per phase, [0.5][1] percent accuracy.

            - kW hours.

Retain first subparagraph below for the Kohler APM603 controller.

            - Generator duty level (actual kW loading divided by kW nameplate).

          - Service Data: Stored in the controller and available for display.

            - Generator model number and serial number.

Retain first three subparagraphs below for the Kohler APM603 controller.

            - ECM serial number.

            - Alternator part number.

            - Engine model number and serial number.

            - Controller serial number and firmware version.

          - Operational Records: Stored in controller beginning at system startup.

            - Total run-time hours.

            - Total loaded hours.

            - Total kW hours.

            - Controller run-time hours.

            - Number of starts.

Retain first eight subparagraphs below for the Kohler APM603 controller.

            - Total unloaded hours.

            - Controller hours.

            - ECM run-time hours.

            - Number of crank attempts.

            - Last crank duration.

            - Last start runtime duration.

            - Last start date and time.

            - Last stop date and time.

Retain first subparagraph below for the Kohler APM603 controller.

          - Maintenance Records: Stored in controller beginning at system startup, user resettable to zero.

            - Total run-time hours since last maintenance.

            - Total loaded hours since last maintenance.

            - Total unloaded hours since last maintenance.

            - Total kW hours since last maintenance.

          - Controls and Protective Devices: Controls, shutdown devices, and common visual alarm indication, including the following:

            - Mode selector switch not in automatic position.

            - Overcrank shutdown.

            - Low lubricating-oil pressure warning.

            - Low lubricating-oil pressure shutdown.

            - Low coolant temperature warning.

First subparagraph below is a common optional feature.

            - High engine temperature warning.

            - High engine temperature shutdown.

            - Overspeed shutdown.

            - Low fuel pressure shutdown.

            - Low fuel main tank.

              - Low-fuel-level alarm to be initiated when the level falls below that required for operation for duration required [for the indicated EPSS class] [in "Fuel Tank Capacity" Subparagraph in "Diesel Fuel-Oil System" Article].

              - Critically low-fuel-level warning.

First subparagraph below is an optional feature for Level 1 engines.

            - Coolant low-level shutdown device.

First two subparagraphs below are optional features not required by NFPA 110.

            - Coolant high-temperature warning.

            - Coolant high-temperature shutdown.

            - ECM Digital Trouble Codes warnings.

            - ECM Digital Trouble Codes shutdown.

            - Loss of ECM Communications shutdown.

            - ECM mismatch shutdown.

Retain first four subparagraphs below for Level 1 battery-start engines. Consider retaining them for Level 2 systems also.

            - Battery high-voltage warning.

            - Battery-charger malfunction warning.

            - Battery low-voltage warning.

            - Remote manual stop shutdown.

            - Local manual stop shutdown.

            - Alternator protection shutdown.

            - Overcurrent warning.

            - Overcurrent shutdown.

            - Under frequency warning.

            - Under frequency shutdown.

            - Over frequency warning.

            - Over frequency shutdown.

            - Over power warning.

            - Over power shutdown.

            - Under voltage warning.

            - Under voltage shutdown.

            - Over voltage warning.

            - Over voltage shutdown.

            - User-defined input warning.

            - User-defined input shutdown.

            - No oil pressure signal shutdown.

            - No speed sensor signal shutdown.

            - Fail-to-start shutdown.

Features in "Connection to Datalink" Paragraph below facilitate connection to building automation system or building control and monitoring system. Coordinate with Drawings and Section covering data transmission and data terminals.

        - Connection to Datalink:

Kohler APM402 controller is capable of ModBus RTU communications and requires optional Modbus/ Ethernet converter for Modbus TCP communications.

          - Provide connections for datalink transmission of indications to remote data terminals via [ModBus RTU] [ModBus TCP] [BACnet] [SNMP] <Insert other data protocol>. Data system connections to terminals are covered in Section 260913 "Electrical Power Monitoring and Control."

        - Supporting Items: Sensors, transducers, terminals, relays, and other devices located on engine or generator unless otherwise indicated.

Coordinate "Remote Emergency-Stop Switch" Paragraph below with Drawings and NFPA 70.

        - Remote Emergency-Stop Switch: Wall mounted unless otherwise indicated. Push button must be permanently labeled and protected from accidental operation.

        - Remote Alarm Annunciator: LED indicator light labeled with proper alarm conditions will identify each alarm event, and a common audible signal will sound for each alarm condition in accordance with NFPA 110. The silencing switch in face of panel will silence signal without altering visual indication. Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset. Controls to include "Lamp Test" momentary switch wired to illuminate all LED indicator lights regardless of alarm state while switch is on. Cabinet and faceplate are surface- or flush-mounting type to suit mounting conditions indicated.

Retain paragraph below if NFPA 70 edition 2017 or later is required by Project.

        - Start Signal Wiring Integrity Monitor: UL-listed modular system to monitor condition of generator remote start circuit(s), annunciate faults, and start generator in accordance with NFPA 70, Article 700.10(D)(4).

          - Output Contacts: Two form "C" contacts, one for engine start and one for start circuit alarm.

      - GENERATOR OVERCURRENT AND FAULT PROTECTION

        - Overcurrent protective devices to be coordinated to optimize selective tripping when a short circuit occurs.

Retain first two subparagraphs below for standby generators.

          - Overcurrent protective devices for the entire EPSS to be coordinated to optimize selective tripping when a short circuit occurs. Coordination of protective devices considers both utility and EPSS as the voltage source.

          - Overcurrent protective devices for the EPSS to be accessible only to authorized personnel.

        - Generator Overcurrent Protective Device:

Retain one or more subparagraphs in this article to specify disconnect switch(es) and protective devices for the generator (alternator) component of engine generator. Revise as required to accommodate multiple output devices.

Typically, retain first subparagraph below for units smaller than 200 kW where initial cost is a concern.

          - Molded-case circuit breaker, thermal-magnetic type; [80] [100] percent rated; complying with UL 489:

            - Tripping Characteristic: Designed specifically for generator protection.

            - Trip Rating: Matched to generator output rating.

Retain "Shunt Trip" Subparagraph below if required for the operation of additional protective relays or devices.

            - Shunt Trip: Connected to trip breaker when engine generator is shut down by other protective devices.

            - Mounting: Adjacent to, or integrated with, control and monitoring panel.

          - Molded-case circuit breaker, electronic-trip type; [80] [100] percent rated; complying with UL 489:

            - Tripping Characteristics: Adjustable long-time and short-time delay and instantaneous.

            - Trip Settings: Selected to coordinate with generator thermal damage curve.

Retain "Shunt Trip" Subparagraph below if required for the operation of additional protective relays or devices.

            - Shunt Trip: Connected to trip breaker when engine generator is shut down by other protective devices.

            - Mounting: Adjacent to, or integrated with, control and monitoring panel.

Insulated-case, electronic-trip breakers in first subparagraph below are susceptible to vibration and should be mounted in a separate enclosure not mounted on the generator skid.

          - Insulated-case circuit breaker, electronic-trip type; [80] [100] percent rated; complying with UL 489:

            - Tripping Characteristics: Adjustable long-time and short-time delay and instantaneous.

            - Trip Settings: Selected to coordinate with generator thermal damage curve.

Retain "Shunt Trip" Subparagraph below if required for the operation of additional protective relays or devices.

            - Shunt Trip: Connected to trip breaker when engine generator is shut down by other protective devices.

            - Mounting: Adjacent to, or integrated with, control and monitoring panel.

Retain subparagraph below if generator is protected by feature described in "Generator Protector" Paragraph.

          - Molded-Case-Type Disconnect Switch:

            - Trip Rating: Matched to generator output rating.

Retain "Shunt Trip" Subparagraph below if required for the operation of additional protective relays or devices.

            - Shunt Trip: Connected to trip switch when signaled by generator protector or by other protective devices.

Protection scheme specified in "Generator Protector" Paragraph below requires controller to be listed as a current protection device per UL 6200, consult manufacturers. Microprocessor-based generator protectors in paragraph are susceptible to vibration and should be mounted in a separate enclosure not mounted on the generator skid.

        - Generator Protector: Microprocessor-based unit to continuously monitor current level in each phase of generator output, integrate generator heating effect over time, and predict when thermal damage of alternator will occur. When signaled by generator protector or other engine generator protective devices, a shunt-trip device in the generator disconnect switch opens the switch to disconnect the generator from load circuits. Protector performs the following functions:

Coordinate load shedding actions in subparagraphs below with Drawings. Indicate which loads will be shed on generator overload and sequence of action if there is more than one load that will be shed.

          - Initiates a generator overload alarm when generator has operated at an overload equivalent to 110 percent of full-rated load for 60 seconds. Indication for this alarm is integrated with other engine generator malfunction alarms. Contacts to be available for load shed functions.

          - Under three-phase fault conditions, generator to supply 300 percent of rated full-load current for up to 10 seconds.

Retain first subparagraph below for Kohler Power Systems APM603 controller, providing overcurrent protection in accordance with UL 6200.

          - Tested to AC output short-circuit requirements.

Retain "Energy Reduction Maintenance Switch/Mode" Subparagraph below in accordance with NEC 240.87 for generators exceeding 1200 A rated output.

          - Energy Reduction Maintenance Switch/Mode.

Retain "Generator Protective Relay" Paragraph below if the Project requires an independent protective relay. This is typically required for large systems with multiple generators operating in parallel.

        - Generator Protective Relay: Multifunctional, microprocessor-based relay systems complying with IEEE C37.90.

          - Standard generator protective functions for shutdown with user-adjustable limits and time delays:

            - Over Voltage (ANSI Device 59):

              - User-Adjustable Pickup: 100 to 130 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

            - Under Voltage (ANSI Device 27):

              - User-Adjustable Pickup: 70 to 100 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

            - Over Frequency (ANSI Device 81O):

              - User-Adjustable Pickup: 100 to 140 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

            - Reverse Power (ANSI Device 32R):

              - User-Adjustable Pickup: Zero to 50 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

            - Over Power (ANSI Device 32O):

              - User-Adjustable Pickup: 90 to 150 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

            - Loss of Field (ANSI Device 40 Reverse VARS):

              - User-Adjustable Pickup: 10 to 100 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

            - Overcurrent with Voltage Range:

              - User-Adjustable Range: 100 to 200 percent.

              - User-Adjustable Time Delay: Zero to 120 seconds.

Retain "Ground-Fault Indication" Paragraph below and coordinate with Drawings for legally required emergency engine generators rated 1000 A or more at 277/480 V.

        - Ground-Fault Indication: Comply with NFPA 70, "Emergency System" signals for ground fault.

Retain one of two subparagraphs below. Retain first for emergency and legally required standby systems. Retain second for optional standby generator systems.

          - Indicate ground fault with other engine generator alarm indications.

          - Trip generator protective device on ground fault.

Retain "Generator Paralleling" Article below if required. Select the Kohler Power Systems APM 603 for this functionality.

      - GENERATOR PARALLELING

        - Capable of paralleling with other generators through a dedicated communication link between the controllers.

        - Support up to eight generators on a common bus.

        - Support paralleling a single generator with a utility source using kW, kVAR, and power factor settings.

        - Synchronization:

          - First-on logic to determine which generator will close to the dead bus first.

          - Synchronization logic to allow matching of voltage, frequency, and phase before closing circuit breaker or contactor to connect the generator to the bus including the following methods:

            - Automatic: Synchronize and close breaker.

            - Sync-Check: Synchronize and no closure.

            - Permissive: No active synchronization, allows manual close if generator is synchronized with bus.

          - Fail-to-sync alarm generated if automatic synchronization is not successful within a user-adjustable time period.

          - Active synchronization will continue after expiration of the fail-to-sync time delay.

          - Specifically designed interface screen to actively display synchronizing parameters for both generator and bus when synchronizing including:

            - Voltage.

            - Frequency.

            - Slip.

            - Phase angle.

            - Phase rotation.

        - Load Sharing:

          - Actively share real and reactive power between all generators connected to common bus on a per-unit or percentage basis.

          - Soft loading and unloading of generator within the isolated generator bus.

          - Capable of droop control.

        - Circuit Breaker/Contactor Control:

          - Capable of directly operating a circuit breaker or contactor to connect or disconnect from the common bus.

          - Normally closed (fail-safe) contact for trip to ensure paralleling device remains open until all conditions are met to allow closure.

          - Normally open contact to provide energizing signal to close paralleling device.

          - Fail-to-close alarm generated after one unsuccessful close attempt.

          - Fail-to-close shutdown after a user-adjustable number of attempts.

        - Generator Management:

          - Automatically start or stop generators based on load demand or state of other generators.

            - Start power.

            - Stop power.

            - Start accumulator.

            - Stop accumulator.

            - Total online capacity.

            - Total available capacity.

            - Total bus power.

            - Total bus capacity.

            - Negotiated order.

            - Stopped by generator management.

            - Start command.

          - Generator management configurable to operate based on:

            - Engine run time.

            - Fuel level.

            - User-assigned order.

          - User programmable disconnect point in kW, below which the generator device will trip.

      - ALTERNATOR, EXCITER, AND VOLTAGE REGULATOR

        - Comply with NEMA MG 1.

        - Maximum Temperature Rise: [80 deg C] [105 deg C] [130 deg C] at full load over 40C ambient.

        - Drive: Alternator shaft to be directly connected to engine shaft. Exciter to be rotated integrally with alternator rotor.

        - Electrical Insulation: Class H.

Retain "Stator-Winding Leads" Paragraph below if a "reconnectable" alternator is required by Project to allow the leads to be reconnected in the field in series or parallel to change between delta and wye configurations.

        - Stator-Winding Leads: Brought out to terminal box to permit future reconnection for other voltages if required.

        - Construction to prevent mechanical, electrical, and thermal damage due to vibration, overspeed up to 125 percent of rating, and heat during operation.

        - Enclosure: Dripproof.

        - Voltage Regulator: Microprocessor-based, high-speed digital voltage regulator, separate from exciter, with three-phase, true RMS sensing, providing performance as specified [ and as required by NFPA 110].

          - Maintain steady-state voltage within 0.25 percent from no load to full load.

          - Adjusting Feature on Control and Monitoring Panel: Provide plus or minus 10 percent adjustment of output-voltage operating band.

Retain "Alternator Strip Heater" Paragraph below for high-humidity environments to limit condensation in alternator windings.

        - Alternator Strip Heater: Thermostatically controlled unit arranged to maintain stator windings above dew point.

Retain "Windings" and "Subtransient Reactance" paragraphs below for units specified for "critical" performance. Coordinate with "Engine Generator Performance" or "Engine Generator Performance for Sensitive Loads" Paragraph in "Engine Generator Assembly Description" Article.

        - Windings: Two-thirds pitch stator winding and fully linked amortisseur winding.

        - Subtransient Reactance: [16] <Insert number> percent, maximum.

      - LOAD BANK

        - Description:

Retain one of two subparagraphs below. Retain first subparagraph and revise for resistive or resistive and reactive load elements; retain second subparagraph for resistive-only load bank skid mounted between the radiator and the exhaust shroud. Coordinate with Drawings.

          - Permanent, outdoor, weatherproof, remote-controlled, forced-air-cooled, [resistive] [resistive and reactive] unit capable of providing a balanced three-phase, delta-connected load to engine generator at [30] [100] <Insert number> percent rated-system capacity, at [80] <Insert number> percent power factor, lagging.[ Unit may contain separate resistive and reactive load banks controlled by a common control panel.] Unit to be capable of selective control of load in 25 percent steps and with minimum step changes of approximately 5 and 10 percent available.

          - Permanent, radiator-mounted [, resistive] unit capable of providing a balanced three-phase, delta-connected load to engine generator at [30] [50] [70] <Insert number> percent rated-system capacity. Unit to be capable of selective control of load in 25 percent steps of load-bank rating and with minimum step changes of approximately 5 and 10 percent available.

        - Regulatory Requirements:

          - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction and marked for intended location and application.

          - <Insert requirements>.

        - General Characteristics:

For assistance with finding-guide information for UL category control numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com.

          - Reference Standards: UL CCN NMTR and UL 508.

        - Resistive Load Elements: Corrosion-resistant chromium alloy with ceramic and stainless-steel supports. Elements to be double insulated and designed for repetitive on-off cycling. Elements to be mounted in removable aluminized-steel heater cases. Galvanized steel is prohibited. The element’s maximum resistance to be between 100 and 105 percent of rated resistance.

        - Reactive Load Elements: Epoxy-encapsulated reactor coils.

        - Load-Bank Heat Dissipation: Integral fan with totally enclosed motor provides uniform cooling airflow through load elements. Airflow and coil operating current to be such that, at maximum load, with ambient temperature at the upper end of specified range, load-bank elements operate at not more than 50 percent of maximum continuous temperature rating of resistance elements.

        - Load-Element Switching: Remote-controlled contactors switch groups of load elements. Contactor coils are rated 120 V. Contactors to be located in a separate NEMA 250, Type 3R enclosure within load-bank enclosure, accessible from exterior through hinged doors with tumbler locks.

        - Contactor Enclosures: Heated by thermostatically controlled strip heaters to prevent condensation.

        - Load-Bank Enclosures: NEMA 250, Type 3R, aluminized steel complying with NEMA ICS 6. Louvers at cooling-air intake and discharge openings prevent entry of rain and snow. Openings for airflow to be screened with 1/2-inch- (13-mm-) square, galvanized-steel mesh. Reactive load bank includes automatic shutters at air intake and discharge. Components other than resistive elements to receive exterior epoxy coating with compatible primer. Comply with requirements in Section 099600 "High-Performance Coatings."

        - Protective Devices: Power input circuits to load banks to be fused, and fuses selected to coordinate with generator circuit breaker. Fuse blocks to be located in contactor enclosure. Cooling airflow and overtemperature sensors automatically shut down and lock out load bank until manually reset. Safety interlocks on access panels and doors disconnect load power, control, and heater circuits. Fan motor to be separately protected by overload and short-circuit devices. Short-circuit devices to be noninterchangeable fuses with 200,000-A interrupting capacity.

Coordinate "Load-Bank Remote-Control Panel" and "Control Sequence" paragraphs below with Drawings.

        - Load-Bank Remote-Control Panel: Separate from load bank in NEMA 250, Type 1 enclosure with a control power switch and pilot light, and switches controlling groups of load elements.

Retain "Control Sequence" Paragraph below if load bank is used in automatic exercising of generator. Coordinate with Section covering remote-controlled switch, contactor, or electrically operated circuit breaker used to switch load bank to generator output. Switching device is typically not part of equipment specified in this Section.

        - Control Sequence: Control panel may be preset for adjustable single-step loading of generator during automatic exercising.

      - OUTDOOR ENGINE GENERATOR ENCLOSURE

        - Description:

Retain one of three subparagraphs below and coordinate with Drawings to define basic outdoor-enclosure type. Revise to specify enclosure features required. Coordinate requirements for water, fuel, power, controls, and alarms with Drawings.

          - Vandal-resistant, [sound attenuated,] weatherproof steel enclosure, with 14-gauge- (2-mm-) thick walls, wind resistant. Multiple panels to be lockable and provide adequate access to components requiring maintenance, minimum two doors per side. Access to controller and main line circuit breaker in accordance with NFPA 70. Panels to be removable by one person without tools. Instruments and controls to be mounted within enclosure.

          - Vandal-resistant, sound-attenuated, weatherproof aluminum enclosure with 0.125-inch- (3-mm-) thick walls; wind resistant. Multiple panels to be lockable and provide adequate access to components requiring maintenance, minimum two doors per side. Access to controller and main line circuit breaker in accordance with NFPA 70. Panels to be removable by one person without tools. Instruments and controls to be mounted within enclosure.

Coordinate subparagraph below with Drawings showing features, construction details, and equipment arrangement.

          - Prefabricated or pre-engineered, aluminum-clad, integral structural-steel-framed, walk-in enclosure; erected on concrete foundation.

        - Source Limitations: Obtain enclosure from engine-driven generator manufacturer.

Revise wind speed in "Structural Design and Anchorage" Paragraph below to suit local conditions. Select Kohler Power System's aluminum level 2 sound enclosures for 186 mph (299 kph) wind loading and/ or hurricane rating.

        - Structural Design and Anchorage: Comply with ASCE/SEI 7 for wind loads up to [150 mph (241 kph)] [186 mph (299 kph)].

        - Hurricane-Rated Aluminum Sound Enclosure:

          - Constructed in accordance with the Florida Building Code.

          - Enclosures are tested and certified in accordance with the following standards:

            - Large Missile Impact Level E (FBC TAS 201-94).

            - Uniform Static Air Pressure (FBC TAS 202-94).

            - Cyclic Wind Pressure Loading (FBC TAS 203-94).

            - Ultimate Design Pressure - Wall Panels ± 65PSF.

            - Ultimate Design Pressure - Roof Panels ± 100PSF.

          - Enclosures must be tested and certified by a certified third party.

        - Minimum Snow Load Rating: 70 psf (33.5 kPa).

        - Seismic Design: Comply with seismic requirements in Section 260548.16 "Seismic Controls for Electrical Systems."

        - Insulation Flammability Classification: UL 94 HF1.

        - Muffler Location: Complete exhaust system located within enclosure.

        - Engine-Cooling Airflow through Enclosure: Maintain temperature rise of system components within required limits.

        - Access doors and panels rubber sealed to prevent water intrusion and minimize noise.

        - Hinged Doors: Lockable; keyed alike with recessed locks.

        - External, weatherproof, recessed-mounted emergency stop pushbutton.

- Retain the following six paragraphs below only when required by the project. These are optional features.

        - Stainless steel latches, hinges, and hardware on external panels of enclosure.

        - Basic Electrical Package:

          - Load Center: [100A single-phase] [125A three-phase], [120/240 V ac] [120/208 V ac].

          - GFCI-duplex receptacles: Two 20 A, 125 V ac.

          - AC Lighting: Two weather-resistant LED lighting maintained with control switches at each access door.

        - DC Lighting: Provide weather-resistant LED lighting, powered from starting battery on fused circuit with 0-60 minute "No-Lock-On" timer.

Retain "Space Heater" Paragraph below for Kohler enclosure and coordinate with gas piping and controls to maintain warmer temperature inside the enclosure in cold ambient conditions. Space heater in an enclosure for an engine generator should be electrically powered via a circuit from the normal power supply. Basic Electrical Package required.

        - Space Heater: Thermostatically controlled and sized to prevent condensation with adjustable louvers offering down flow and horizontal air tuning.

Retain one or both Subparagraphs below if required by project. Consider specifying automatic dampers on both inlet and exhaust if space heaters are required. See Section 089116 "Operable Wall Louvers" and Section 089119 "Fixed Louvers" for engine generator, air-inlet, and exhaust louvers.

        - Fixed Louvers, Dampers, and Ventilation.

          - Fixed Louvers: Engine, cooling-air inlet and discharge. Stormproof and drainable louvers limiting entry of rain and snow.

          - Dampers: [Motorized, aluminum inlet] [Motorized, galvanized steel inlet] [Gravity-activated, aluminum outlet] damper[s] at engine cooling-air inlet and outlet. Dampers to be closed to reduce enclosure heat loss in cold weather when unit is not operating.

Revise "Ventilation" Subparagraph below if forced ventilation rather than convection ventilation is required.

          - Ventilation: Provide temperature-controlled, wall-mounted exhaust fan interlocked to prevent operation when engine is running.

Retain "Catwalk" Paragraph below if subbase tank is 19 inches (480 mm) or higher.

        - Catwalk: Full-length catwalk with stairs and railings for access to all doors along both sides level with the bottom of the enclosure is required for maintenance. Treads to be slip-resistant. Comply with 29 CFR 1910.23.

      - REMOTE RADIATOR MOTORS

Retain this article for engine generators with remote radiators. Give careful consideration to the location and supply source for the overcurrent-protective device dedicated for this equipment.

        - Description: NEMA MG 1, Design B, medium-induction, random-wound, squirrel-cage motor.

        - Efficiency: Energy efficient, as defined in NEMA MG 1.

        - Service Factor: 1.15.

        - Bearings: Regreasable, shielded, antifriction ball bearings suitable for radial and thrust loading.

        - Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

        - Temperature Rise: Match insulation rating.

        - Code Letter Designation:

Starting codes in first subparagraph below are adequate for most variable-torque loads encountered in HVAC applications; 15 hp is a common breakpoint in rating among manufacturers when Code F and Code G apply. Retain both subparagraphs and options below unless Project conditions or equipment characteristics dictate otherwise.

          - Motors [15] <Insert number> HP and Larger: NEMA starting Code F or Code G.

          - Motors Smaller Than [15] <Insert number> HP: Manufacturer's standard starting characteristic.

        - Enclosure Material: Cast iron for motor frame sizes 324T and larger; rolled steel for motor frame sizes smaller than 324T.

        - Motor starter: Full-voltage non-reversing (across the line) motor starter installed and wired to the output terminals of the generator per NFPA 70.

      - VIBRATION ISOLATION DEVICES

Review local seismic standard to ensure compliance.

        - Elastomeric Vibration Isolators: Oil- and water-resistant elastomer neoprene or natural rubber, molded with a nonslip pattern and baseplates of sufficient stiffness for uniform loading over pad area, and factory cut to sizes that match requirements of supported equipment. Compliant with ISO 8528-9.

        - Comply with requirements in Section 232116 "Hydronic Piping Specialties" for vibration isolation and flexible connector materials for steel piping.

        - Comply with requirements in Section 233113 "Metal Ducts" for vibration isolation and flexible connector materials for exhaust shroud and ductwork.

        - Vibration isolation devices may not be used to accommodate misalignments or to make bends.

      - FINISHES

        - Indoor and Outdoor Enclosures and Components: Heavy-duty, high-durability, fade-, scratch- and corrosion-resistant finish achieved through a multi-stage finishing process from the genset manufacturer including:

          - Pre-cleaning: Enclosure components cleaned with a two-stage alkaline cleaning process to remove grease, grit, and grime from parts then subjected to a Zirconium-based conversion coating process to prepare the metal for electrocoat (e-coat) adhesion.

          - Primer: All enclosure parts to receive 100 percent epoxy primer electrocoat (e-coat) with high-edge protection.

          - Finish Coating: Powder-baked paint for superior finish, durability, and appearance.

          - Minimum Enclosure Corrosion Resistance: 3000 hours salt spray test in accordance with ASTM B117.

          - Powder coat for fading and abrasion resistance.

        - Subbase Tank: Polyurea-texturized rubber coating for corrosion protection and adequate surface grip from the genset manufacturer.

      - SOURCE QUALITY CONTROL

        - Prototype Testing: Factory test engine generator using same engine model, constructed of identical or equivalent components and equipped with identical or equivalent accessories.

          - Tests: Comply with IEEE 115[ and with NFPA 110, Level 1 Energy Converters].

Tests in "Project-Specific Equipment Tests" Paragraph below are in addition to the prototype tests listed above. They do not test the unit under the full range of conditions as the above tests, but are useful to provide assurance that the specific unit supplied to Project meets most of the critical parameters that can be tested without stressing the unit.

        - Project-Specific Equipment Tests: Before shipment, factory test engine generator and other system components and accessories manufactured specifically for this Project. Perform tests at rated load and power factor. Include the following tests:

Tests in first seven subparagraphs below are considered "standard" by Kohler Power Systems and are performed at the factory even if not required by this Specification.

          - Test generator, exciter, and voltage regulator as a unit.

          - Load Test: 25, 50, 75 and 100 percent rated load.

          - Single-step load pickup.

          - Safety shutdown.

          - Overcrank.

          - Locked rotor.

          - Mechanical Readings: Oil pressure, ambient temperature, and coolant temperature.

Tests in first four subparagraphs below are considered "specialized" by Kohler Power Systems and typically imply cost or schedule impacts.

          - Test components and accessories furnished with installed unit that are not identical to those on tested prototype to demonstrate compatibility and reliability.

          - Maximum power.

          - Voltage regulation.

          - Transient and steady-state governing.

Retain first subparagraph below if factory tests will be witnessed by Owner's representative.

          - Provide 14 days' advance notice of tests and opportunity for observation of tests by Owner's representative.

Coordinate subparagraph below with "Informational Submittals" Article.

          - Report factory test results within 10 days of completion of test.

- EXECUTION

      - EXAMINATION

        - Examine areas, equipment bases, and conditions, with Installer present, for compliance with requirements for installation and other conditions affecting packaged engine generator performance.

        - Examine roughing-in for piping systems and electrical connections. Verify actual locations of connections before packaged engine generator installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

Delete "Interruption of Existing Electrical Service" Paragraph below if no interruption of existing electrical service is required.

        - Interruption of Existing Electrical Service: Do not interrupt electrical service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electrical service in accordance with requirements indicated:

          - Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> working days in advance of proposed interruption of electrical service.

          - Do not proceed with interruption of electrical service without [Architect's] [Construction Manager's] [Owner's] written permission.

      - INSTALLATION

        - Comply with NECA 1 and NECA 404.

        - Comply with packaged engine generator manufacturers' written installation and alignment instructions [ and with NFPA 110].

Verify, with Project participants, which concrete Section in "Equipment Mounting" Paragraph below will be used for concrete pads and bases.

        - Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases. NFPA 110 requires indoor Level 1 engine generators to be installed in a dedicated room with 1- or 2-hour fire rating. Indoor installations also require fuel storage within the building and large airflows for cooling and combustion.

          - Install engine generators on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

          - Coordinate size and location of concrete bases for engine generators. Cast anchor-bolt inserts into bases. Concrete, reinforcement, and formwork requirements are specified with concrete.

Retain either option in first subparagraph below for mounting equipment outside or to accommodate seismic mounting. Consult authorities having jurisdiction for requirements. Verify minimum deflection with structural or seismic engineer and/or per drawings.

          - Install [engine generator with a skin-tight enclosure] [engine generator with a walk-in enclosure].

          - Remote Radiators:

            - Install remote radiator with [elastomeric isolator pads] [restrained spring isolators] on [concrete base on grade] [roof equipment supports on roof].

Retain subparagraph below for remote radiators located on roof.

            - Coordinate size and location of roof curbs, equipment supports, and roof penetrations for remote radiators. These items are specified in Section 077200 "Roof Accessories."

        - Install packaged engine generator to provide access, without removing connections or accessories, for periodic maintenance.

Delete "Cooling System" Paragraph below if radiator is engine mounted.

        - Cooling System: Install Schedule 40 black steel piping with welded joints for cooling water piping between engine generator and [heat exchanger] [remote radiator]. Piping materials and installation requirements are specified in Section 232113 "Hydronic Piping."

          - Install isolating thimbles where exhaust piping penetrates combustible surfaces. Provide a minimum of 9 inches (225 mm) of clearance from combustibles.

          - Insulate cooling-system piping and components in accordance with requirements in Section 230719 "HVAC Piping Insulation."

        - Exhaust System: Install Schedule 40 black steel piping with welded joints and connect to engine muffler. Install thimble at wall. Piping sized in accordance with allowable back pressure for the engine and indicated on mechanical plans.

          - Piping materials and installation requirements are specified in Section 232113 "Hydronic Piping."

          - Install flexible connectors and steel piping materials in accordance with requirements in Section 232116 "Hydronic Piping Specialties."

          - Insulate muffler/silencer and exhaust system components in accordance with requirements in Section 230719 "HVAC Piping Insulation."

See Section 077200 "Roof Accessories" for roof curbs, piping supports, and roof-penetration boots.

          - Install isolating thimbles where exhaust piping penetrates combustible surfaces with a minimum of 9 inches (225 mm) of clearance from combustibles.

Coordinate "Drain Piping" Paragraph below with Drawings.

        - Drain Piping: Install condensate drain piping to muffler drain outlet full size of drain connection with a shutoff valve, stainless steel flexible connector, and Schedule 40 black steel.

          - Piping materials and installation requirements are specified in Section 232113 "Hydronic Piping."

          - Drain piping valves, connectors, and installation requirements are specified in Section 232116 "Hydronic Piping Specialties."

        - Fuel Piping:

          - Diesel storage tanks, tank accessories, piping, valves, and specialties for fuel systems. are specified in Section 231113 "Facility Fuel-Oil Piping."

          - Copper and galvanized steel may not be used in the fuel-oil piping system.

        - Install electrical devices furnished by equipment manufacturers but not specified to be factory mounted.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Piping installation requirements. are specified in other Sections. Drawings indicate general arrangement of piping and specialties.

        - Connect fuel, cooling-system, and exhaust-system piping adjacent to packaged engine generator to allow space for service and maintenance.

Coordinate first two paragraphs below with Section 230719 "HVAC Piping Insulation."

Coordinate first paragraph below with Section 232116 "Hydronic Piping Specialties."

        - Connect cooling-system water piping to engine generator and [remote radiator] [heat exchanger] with flexible connectors.

        - Connect engine exhaust pipe to engine with flexible connector.

        - Connect fuel piping to engines with a gate valve and union and flexible connector.

        - Ground equipment in accordance with [NFPA 70.] [Section 260526 "Grounding and Bonding for Electrical Systems."]

        - Connect wiring in accordance with [NFPA 70.] [Section 260519 "Low-Voltage Electrical Power Conductors and Cables."] Provide flexible conduit routed to the engine generator from a stationary element.

        - Balance single-phase loads to obtain a maximum of 10 percent unbalance between any two phases.

      - IDENTIFICATION

        - Identify system components in accordance with Section 230553 "Identification for HVAC Piping and Equipment" and Section 260553 "Identification for Electrical Systems."

        - Install a sign indicating the generator [neutral is bonded to the main service neutral at the main service location] [is installed as a separately derived source per NFPA 70].

      - FIELD QUALITY CONTROL

        - Testing Agency:

Retain one of first four subparagraphs below. Retain first subparagraph below if Owner will hire an independent testing agency. Retain second subparagraph below to require Contractor to hire an independent testing agency. Retain third subparagraph below to require a factory-authorized service representative to perform tests and inspections. Retain fourth subparagraph below to require Contractor to perform tests and inspections and, if required, retain option to require Contractor to arrange for the assistance of a factory-authorized service agent.

          - Owner will engage a qualified testing agency to perform tests and inspections.

          - Engage a qualified testing agency to perform tests and inspections.

          - Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

          - Perform tests and inspections [ with the assistance of a factory-authorized service representative].

        - Tests and Inspections:

Retain test requirements below with any combination of paragraphs above. The following tests and inspections are derived from NETA Acceptance Testing Specification (ATS). Review NETA ATS and other standards listed, and revise subparagraphs below.

          - Perform tests recommended by manufacturer and each visual and mechanical inspection and electrical and mechanical test listed in first two subparagraphs below, as specified in NETA ATS. Certify compliance with test parameters.

            - Visual and Mechanical Inspection:

              - Compare equipment nameplate data with Drawings and the Specifications.

              - Inspect physical and mechanical condition.

              - Inspect anchorage, alignment, and grounding.

              - Verify that the unit is clean.

            - Electrical and Mechanical Tests:

              - Verify phase rotation, phasing, and synchronized operation as required by the application.

              - Functionally test engine shutdown for low oil pressure, overtemperature, overspeed, and other protection features as applicable.

          - NFPA 110 Acceptance Tests: Perform tests required by NFPA 110 that are additional to those specified here, including, but not limited to, single-step full-load pickup test.

          - Battery Tests: Equalize charging of battery cells in accordance with manufacturer's written instructions. Record individual cell voltages.

            - Measure charging voltage and voltages between available battery terminals for full-charging and float-charging conditions. Check electrolyte level and specific gravity under both conditions.

            - Test for contact integrity of all connectors. Perform an integrity load test and a capacity load test for the battery.

            - Verify acceptance of charge for each element of the battery after discharge.

            - Verify that measurements are within manufacturer's specifications.

          - Battery-Charger Tests: Verify specified rates of charge for both equalizing and float-charging conditions.

          - System Integrity Tests: Methodically verify proper installation, connection, and integrity of each element of engine generator system before and during system operation. Check for air, exhaust, and fluid leaks.

Retain "Exhaust-System Back-Pressure Test" Subparagraph below for long, restricted exhaust systems.

          - Exhaust-System Back-Pressure Test: Use a manometer with a scale exceeding 40-inch wc (120 kPa). Connect to exhaust line close to engine exhaust manifold. Verify that back pressure at full-rated load is within manufacturer's written allowable limits for the engine.

Verify local requirements and delete "Exhaust Emissions Test" Subparagraph below for most projects. Few jurisdictions require this test for emergency or standby engine generators.

          - Exhaust Emissions Test: Comply with applicable government test criteria.

          - Voltage and Frequency Transient Stability Tests: Use recording oscilloscope to measure voltage and frequency transients for 50 percent step-load increases and decreases and verify that performance is as specified.

Retain "Noise Level Tests" Subparagraph below for projects with specific site requirements. Coordinate with Drawings and with requirements in "Action Submittals," "Quality Assurance," and "Engine Generator Assembly Description" articles. Note that some noise, such as the engine noise, is directional and siting the generator can have a large impact on the measured noise in some directions.

          - Noise Level Tests: Measure A-weighted level of noise emanating from engine generator installation, including engine exhaust and cooling-air intake and discharge, at [four] [eight] <Insert number> locations [23 ft. (7 m) from edge of the generator enclosure] [on the property line] <Insert location for measurement>, and compare measured levels with required values.

        - Coordinate tests with tests for transfer switches and run them concurrently.

        - Test instruments to have been calibrated within the past 12 months, traceable to NIST Calibration Services, and adequate for making positive observation of test results. Make calibration records available for examination on request.

        - Leak Test: After installation, inspect exhaust, coolant, and fuel systems and test for leaks. Repair leaks and retest until no leaks exist.

        - Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation for generator and associated equipment.

        - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

        - Remove and replace malfunctioning units and [retest] [reinspect] as specified above.

        - Retest: Correct deficiencies identified by tests and observations, and retest until specified requirements are met.

        - Report results of tests and inspections in writing. Record adjustable relay settings and measured insulation resistances, time delays, and other values and observations. Attach a label or tag to each tested component indicating satisfactory completion of tests.

        - Infrared Scanning: After Substantial Completion, but not more than 60 days after final acceptance, perform an infrared scan of each power wiring termination and each bus connection while running with maximum load.

          - Follow-up Infrared Scanning: Perform an additional follow-up infrared scan 11 months after date of Substantial Completion.

          - Instrument: Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

          - Record of Infrared Scanning: Prepare a certified report that identifies terminations and connections checked and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

      - MAINTENANCE SERVICE

Retain this article for critical installations and consider including a provision for submitting a continuing maintenance agreement proposal. Revise starting date if required. Obtain a copy of maintenance agreement before retaining or revising "Initial Maintenance Service" Paragraph below. Maintenance contracts may not be allowed for publicly funded projects.

Verify with Owner that maintenance service is required for Project.

        - Initial Maintenance Service: Beginning at Substantial Completion, maintenance service to include [12] <Insert number> months' full maintenance by skilled employees of manufacturer's authorized service representative. Include quarterly preventive maintenance and exercising to check for proper starting, load transfer, and running under load. Include routine preventive maintenance as recommended by manufacturer and adjusting as required for proper operation. Parts to be manufacturer's authorized replacement parts and supplies.

      - DEMONSTRATION

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain packaged engine generators.

END OF SECTION 263213.13