SECTION 263600 - TRANSFER SWITCHES

Copyright 2022 Kohler Co.  This document is a modification and derivative work of a Masterspec based document licensed to Kohler by Deltek

To view non-printing Editor's Notes (visible in blue font) that provide guidance for editing, click on the ¶ symbol in the paragraph section under the Home menu.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

GENERAL

SUMMARY

Section Includes:

Transfer switch controller.

Standard (open) transition, contactor-type, transfer switches.

Programmed (delayed) transition, contactor-type, transfer switches.

Closed transition, contactor-type, transfer switches.

Standard (open) transition, contactor type, bypass isolation transfer switches.

Programmed (delayed) transition, contactor type, bypass isolation transfer switches.

Closed transition, contactor type, bypass isolation transfer switches.

Service-entrance programmed (delayed) transition, breaker type, transfer switches.

Transfer switch accessories.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

Automatic Transfer Switch (ATS): Device in which a controller manages the entire process, and initiation begins when the controller senses a loss of the primary source. The controller monitors the source voltage and sends a command to the generators to run when the voltage falls below a preset limit for a prescribed period. The controller also monitors the secondary source voltage and frequency, and when these values are within acceptable limits, the switch transfers the load from the primary to the secondary source. When the primary source is reestablished for a prescribed period to ensure stability, the switch may automatically transfer the load back to the primary source. Most critical and life-safety loads require automatic operation as defined by the NEC.

Bypass Isolation Transfer Switch: Transfer switch that incorporates a standard automatic and a manual transfer switch into a single unit. Bypass isolation is used to transfer power to the manual switch to allow servicing of the ATS while maintaining power to connected loads.

Mechanically Operated: Physical handle is used to select between manual and automatic sides of the bypass isolation transfer switch.

Electrically Operated: Push-button controls are used to select between manual and automatic sides of the bypass isolation transfer switch.

Contactor type switching mechanism: Contactors are constructed as an electrically controlled, double-throw switch where a solenoid mechanism opens one set of power contacts while closing a second set.

Enclosures: The following are UL 50 definitions of enclosure types listed in order of protection from least hazardous to most severe conditions.

Type 1: Enclosures constructed for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment and to provide a degree of protection against falling dirt.

Type 3R: Constructed (with knockouts on the sides and bottom) for either indoor or outdoor use to provide protection against falling dirt, rain, sleet, snow, and windblown dust. Will be undamaged by the external formation of ice on the enclosure. Type 3R enclosures are rainproof, which means they are constructed, protected, or treated to prevent beating rain from interfering with the successful operation of the apparatus or result in wetting of live parts and wiring within the enclosure under specified conditions. They are not raintight, which means exposure to beating rain could result in water entering a Type 3R enclosure under certain conditions; nor are they watertight, which means moisture could enter a Type 3R enclosure when subjected to a stream of water under certain conditions.

Type 4: Constructed for either indoor or outdoor use to provide protection against falling dirt, rain, sleet, snow, windblown dust, splashing water, and hose-directed water. Will be undamaged by the external formation of ice on the enclosure.

Type 4X: Same as Type 4 except constructed from corrosion-resistant material. As defined by industry standards, corrosion resistant means constructed to provide a degree of protection against exposure to corrosive agents such as salt spray. Stainless steel is the strongest of the corrosion-resistant materials. It exhibits many of the same resistances attributed to fiberglass materials as well as resistance to highly polar solvents such as acetone and MEK. Type 316 grade stainless steel is an option that provides improved resistance to salt, some acids, and high temperature. Type 316 grade is a strongly recommended choice for marine environments that are within five miles of salt water or otherwise subject to exposure to salt spray. Note that Type 316 grade resistance to sulfates and chorine is less than that provided by Type 304 grade

Type 12: Constructed (without knockouts) for indoor use to provide protection against falling dirt; against circulating dust, lint, fibers, and flying debris; against dripping and light splashing of noncorrosive liquids; and against light splashing and consequent seepage of oil and noncorrosive coolants. Type 12 enclosures are oil resistant, and constructed so oil will not interfere with successful operation of equipment. They are not oiltight, which means oil could enter a Type 12 enclosure under certain conditions.

Insulated-Case Type Switching Mechanism: Provides electronic trip overcurrent protection using UL 1558 listed circuit breakers (100 percent rated).

Manual Transfer Switch: Transfer switch in which the entire process is completed manually by an operator. There is not typically a controller, voltage-sensing equipment, or electrical mechanism used to operate the load transfer. Manual switches are the most basic types of transfer switch and are common in noncritical facilities or applications.

Molded-Case Type Switching Mechanism: Provides thermal-magnetic or electronic trip overcurrent protection using UL 489 listed circuit breakers (80 percent rated).

Non-Automatic Transfer Switch: Transfer switch that is manually initiated by an operator and then an internal device within the switch equipment operates the transfer switch by electric operation. The operator has the ability to determine when to initiate the load transfer, but the actual transfer operation is electrically actuated.

Service Entrance Transfer Switch: Transfer switch that serves as both ATS and utility service disconnect.

Transition Types:

Standard (Open) Transition: Break-before-make transfer. In open transition, the load is disconnected from one normal source before being connected to the alternate emergency source.

Programmed (Delayed) Transition: Break both normal and emergency sides before transfer. The load disconnects from one source, and then pauses in an "off" position before connecting to the alternate source to protect from power surges. The delay allows the magnetic field to decay to a safe level before transferring.

Closed Transition: Make-before-break transfer. The source from which the load is being transferred remains closed until the source to which the load will be transferred is also closed. After both sources are closed, the source from which power is being transferred is opened.

Withstand and Close-On Rating (WCR): The following are the types of transfer switch WCR ratings.

Specific Breaker Rating: Transfer switch that is tested in coordination with specific upstream circuit breakers. Only breakers listed on the transfer switch rating decal may be used.

Time-Based Rating (Any Breaker): Transfer switch that passes the "any breaker" test can withstand a fault of a given magnitude for three cycles. This allows an ATS to be used with any UL 489 circuit breaker.

Short-Time Rating: The short-time ratings require longer-duration application of fault current and are intended for selective coordination purposes, where an extended delay is needed to allow for downstream protective devices to clear a fault closer to its source.

Fuse Disconnect: A device used for limiting the amount of fault current that passes through a system and protects downstream power system components from catastrophic failure. When fault current exceeds the current rating, the circuit is opened, and a new fuse is required to make the system operational again. These devices are typically used when fault current exceeds ratings for other options.

ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for transfer switches.

Include rated capacities, operating characteristics, electrical characteristics, and accessories.

Shop Drawings:

Include plans, elevations, sections, details showing minimum clearances, conductor entry provisions, gutter space, and installed features and devices.

Include material lists for each switch specified.

Single-Line Diagram: Show connections between transfer switch, power sources, and load; and show interlocking provisions for each combined transfer switch and/or bypass/isolation switch.

Retain and revise, if necessary, "Riser Diagram" Subparagraph below if retaining remote annunciators, control panels, or bypass/isolation transfer switches.

Riser Diagram: Show interconnection wiring between transfer switches, annunciators, and control panels.

INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For [manufacturer-authorized service representative] [testing agency].

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

Seismic Qualification Data: Certificates, for transfer switches, accessories, and components, from manufacturer.

Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

Field quality-control reports.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For each type of product to include in emergency, operation, and maintenance manuals.

In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

Features and operating sequences, both automatic and manual.

List of all factory settings of relays; provide relay-setting and calibration instructions, including software, where applicable.

QUALITY ASSURANCE

Manufacturer Qualifications:

ISO 9001 certified for design, development, production, and service of complete product line.

Produced this type of equipment for a period of at least 10 years.

Actively maintaining a 24-hour parts and service organization regularly engaged in maintenance contract programs to perform preventive maintenance and service on equipment like that specified.

Furnish a service agreement that includes system operation under simulated operating conditions; adjustment to the generator set, transfer switch, and switchgear controls as required, and certification in the Owner's maintenance log of repairs made and functional tests performed on all systems.

Transfer switch, engine-driven generator assembly, and paralleling switchgear (if applicable) must be furnished by a single manufacturer, responsible for design, coordination, and testing of the complete system.

Retain "Testing Agency Qualifications" Paragraph below if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements."

Testing Agency Qualifications:

Member company of NETA.

Testing Agency's Field Supervisor: Certified by NETA to supervise on-site testing.

WARRANTY

Manufacturer's Warranty: Manufacturer agrees to repair or replace transfer switch or transfer switch components that fail in materials or workmanship within specified warranty period.

Verify available manufacturer's warranties and warranty periods for units and components.

Warranty Period: <Insert time> years from date of registered startup or commissioning.

Transfer switch and accessories to include a standard one-year warranty against defective material and workmanship in accordance with manufacturer's published warranty from registered startup date.

Retain "Extended Warranty" Subparagraph below for a warranty period that exceeds manufacturer's standard warranty. A comprehensive warranty is defined as including repair parts, labor, and travel to and from the installation site in accordance with manufacturer's published warranty.

Extended Warranty: [Comprehensive two-year] [Limited five-year] [Comprehensive five-year] [Limited 10-year] warranty including repair [parts and labor] [parts, labor, and travel to and from the installation site] in accordance with manufacturer's published warranty.

PRODUCTS

PERFORMANCE REQUIREMENTS

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Kohler Power Systems; transfer switches or comparable product by one of the following:

Caterpillar, Inc.; Electric Power Division.

Generac Power Systems, Inc.

<Insert manufacturer's name>.

Source Limitations: Manufacturer must supply generators, transfer switches, and paralleling switchgear for single-source warranty, parts, and service through a factory authorized representative with factory-trained technicians.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Comply with NEMA ICS 1.

Retain one of first two paragraphs below, or both, if applicable to Project.

Comply with NFPA 99.

Comply with NFPA 110.

Comply with UL 1008 unless requirements of these Specifications are stricter.

Retain first paragraph below when required. This is an optional feature not available with service entrance rated transfer switches.

CSA C22.2, No. 178 certification.

Retain first paragraph below for all transfer switches except electrically operated bypass isolation. This is an optional feature.

Comply with International Building Code (IBC) Seismic Certification.

Retain first paragraph below for California healthcare facilities with mechanically operated bypass isolation and time-based transfer switches only. This is an optional feature.

Comply with Department of Health Care Access and Information (HCAI), formerly known as OSHPD.

Switch Characteristics: Designed for continuous-duty repetitive transfer of full-rated current between active power sources.

Retain the first three subparagraphs for contactor-based transfer switches. Transfer switches used in emergency systems must have mechanically held contacts.

Switch Action: Double throw; mechanically held in both directions.

Contacts: Silver composition or silver alloy for load-current switching. Contactor-style automatic transfer-switch units, rated 800 A and higher, to have separate arcing contacts.

Inspection of all contacts possible from the front of the switch without disassembly of operating linkages and without disconnection of power conductors. Switches rated 800 A and higher must have front removable and replaceable contacts. All stationary and moveable contacts replaceable without removing power conductors or bus bars.

Main and Neutral Lugs: Mechanical type.

Lug Material: Tin-plated aluminum.

Conductor Connectors: Suitable for use with conductor material and sizes.

Ground Lugs and Bus-Configured Terminators: Mechanical type.

Connectors to be marked for conductor size and type in accordance with UL 1008.

Indicated Current Ratings: Apply as defined in UL 1008 for continuous loading and total system transfer, including tungsten filament lamp loads not exceeding 30 percent of switch ampere rating, unless otherwise indicated.

Indicate required ratings on Drawings.

Tested Fault-Current Closing and Short-Circuit Ratings: Adequate for duty imposed by protective devices at installation locations in Project under the fault conditions indicated, based on testing in accordance with UL 1008.

Repetitive Accuracy of Solid-State Controls: All settings to be plus or minus 0.5 percent or better over an operating temperature range of minus 20 to plus 70 deg C.

Resistance to Damage by Voltage Transients: Components meet or exceed voltage-surge withstand capability requirements when tested in accordance with IEEE C62.62. Components meet or exceed voltage-impulse withstand test of NEMA ICS 1.

Electrical Operation: Accomplish by a nonfused, momentarily energized solenoid or electric-motor-operated mechanism. Switches for emergency or standby purposes to be mechanically and electrically interlocked in both directions to prevent simultaneous connection to both power sources unless closed transition or manual transfer.

Neutral: Ampacity and switch rating of neutral path through units to be the nominal rating of circuit in which switch is installed.

Factory Wiring: Train and bundle factory wiring and label, consistent with Shop Drawings, by color code or by numbered or lettered wire and cable markers at terminations.

Designated Terminals: Pressure type, suitable for types and sizes of field wiring indicated.

Power-Terminal Arrangement and Field-Wiring Space: Suitable for top, side, or bottom entrance of feeder conductors as indicated.

Control Wiring: Equipped with lugs suitable for connection to terminal strips.

TRANSFER SWITCH CONTROLLER

Non-Automatic transfer switches only available for standard contactor-based transfer switches.

Requires [Automatic] [Non-Automatic] transfer switch controller.

Retain "Supervised Transfer Switch" Paragraph below if non-automatic transfer switch control is required. Kohler Non-Automatic controllers require Supervised Transfer Switch option.

Supervised Transfer Switch: Provide a door-mounted, three-position, selector switch with Auto, Manual, and Transfer positions.

With the controller set to automatic mode and selector switch in Auto position, the user transfer switch operates normally.

With the controller set to automatic mode and selector switch in Manual position, the user is required to toggle the selector switch to initiate a transfer from emergency to normal position.

With the controller set to non-automatic mode and selector switch in Manual position, the user is required to toggle the selector switch to the transfer position to initiate a transfer in either direction. In this mode, the ATS must not automatically transfer to an acceptable source in the case of source failure.

Display: Integral to controller for viewing all available data and setting desired operational parameters. Operational parameters also available for viewing and control through communications interface port or USB. The following parameters are only adjustable via password-protected programming on the controller:

Nominal line voltage and frequency.

Single- or three-phase sensing.

Operating parameter protection.

Controller capable of sensing phase rotation of both normal and emergency sources. Source is considered unacceptable if phase rotation is not the preferred rotation selected (ABC or BAC). Unacceptable phase rotation indicated on LCD; service required LED and annunciation through the communication protocol and dry contacts. Phase rotation sensing capable of being disabled, if required.

Controller capable of detecting a single phasing condition of a source, even though a voltage may be regenerated by the load. This condition is a loss of phase and considered a failed source.

Source status screens provided for both normal and emergency sources to provide digital readout of voltage on all three phases (phase to phase and phase to neutral), frequency, and phase rotation.

Test Switch: Simulate normal-source failure.

Switch-Position Indicating Lights: Indicate source to which load is connected.

Source-Available Indicating Lights: Supervise sources via transfer-switch normal- and emergency-source sensing circuits.

Normal Power Supervision: Green light with nameplate engraved "Normal Source Available."

Emergency Power Supervision: Red light with nameplate engraved "Emergency Source Available."

Unassigned Auxiliary Contacts: Two normally open, single-pole, double-throw contacts for each switch position, rated 10 A at 240 V(ac).

Transfer Override Switch: Overrides automatic retransfer control so that transfer switch will remain connected to emergency power source regardless of condition of normal source. Pilot light indicates override status.

Controller operates through a period of loss of control power.

Revise pickup, dropout, and time-delay settings in first six subparagraphs below to suit application, and retain required features.

Undervoltage Sensing for Each Phase of Normal [and Alternate ]Source: Sense low phase-to-ground voltage on each phase. Pickup voltage to be adjustable from 85 to 100 percent of nominal, and dropout voltage to be adjustable from 75 to 98 percent of pickup value. Factory set for pickup at 90 percent and dropout at 90 percent.

Overvoltage Sensing for Each Phase of Normal [and Alternate ]Source: Sense low phase-to-ground voltage on each phase. Pickup voltage to be adjustable from 95 to 100 percent of dropout, and dropout voltage to be adjustable from 106 to 135 percent of nominal value. Factory set for pickup at 95 percent and dropout at 110 (600V) or 115 percent.

Voltage Unbalance Sensing for Each Phase of Normal [and Alternate ]Source: Sense low phase-to-ground voltage on each phase. Pickup voltage to be adjustable from 3 to 18 percent of nominal, and dropout voltage to be adjustable from 5 to 20 percent of nominal value. Factory set for pickup at 10 percent and dropout at 20 percent.

Under-frequency: Prevent premature transfer to generator. Pickup frequency to be adjustable from 80 to 95 percent of nominal. Factory set for pickup at 90 percent. Dropout frequency to be adjustable from 95 to 99 percent of nominal. Factory set for pickup at 99 percent of dropout.

Over-frequency: Prevent premature transfer to generator. Pickup frequency to be adjustable from 105 to 120 percent of nominal. Factory set for pickup at 110 percent. Dropout frequency to be adjustable from 101 to 115 percent of nominal. Factory set for dropout at 101 percent.

Time Delays:

Generator start delay settings longer than 15 seconds require an external DC control power supply. Coordinate optional text retained in "Momentary Genset Start Delay" Subparagraph below with transfer switch accessories specified in "External Battery Supply Module" Paragraph.

Momentary Genset Start Delay: Adjustable time delay of zero to [15 seconds] [60 minutes] to override momentary normal source outages and delay all transfer and engine starting signals. Capabile of extended time delay up to 60 minutes by providing an external 12 or 24 V(dc) power supply.

Transfer to Emergency Source: Adjustable from zero to 60 minutes provided on transfer to the emergency source for controlled timing of transfer of loads to emergency. Factory setting is three seconds.

Retransfer to Normal Source: Adjustable from zero to 60 minutes time delay for re-transfer to normal. Time delay automatically bypassed if the emergency source fails and the normal source is acceptable. Factory setting is 15 minutes.

Engine Cool Down: Adjustable from zero to 60 minutes provided on shutdown of engine generator for cool down. Factory setting is five seconds.

Time Delay Outputs: Time delay activated output signals to drive external relay(s) for selective load disconnect and reconnect control. Capable of controlling nine individual output time delays to step loads on after a transfer occurs. Each output individually programmed for independent time delay from zero to 60 minutes. Each sequence independently programmed for transferring from normal to emergency and transferring from emergency to normal.

Retain "Engine Starting Contacts" Subparagraph below if needed to coordinate with engine generator. Do not duplicate control features furnished with generator. Coordinate contacts with engine generator.

Engine Starting Contacts: One isolated and normally closed, and one isolated and normally open; rated 10 A at 32 V(dc) minimum.

Engine Shutdown Contacts:

Retain "Instantaneous" or "Time Delay" Subparagraph below.

Instantaneous: Contact initiates shutdown sequence at remote engine-generator controls after retransfer of load to normal source with no intentional time delay.

Time Delay: Adjustable from zero to five minutes, and factory set for five minutes. Contact initiate shutdown at remote engine-generator controls after retransfer of load to normal source.

Retain "Signal-Before-Transfer Contacts" Paragraph below if required for control to minimize elevator disruption or for other purposes.

Signal-Before-Transfer Contacts: One set of normally open/normally closed dry contacts that operate in advance of retransfer to normal source. Interval adjustable from one to 30 seconds.

Engine-Generator Exerciser: Solid-state, programmable-time switch starts engine generator and transfers load to it from normal source for a preset time, then retransfers and shuts down engine after a preset cool-down period. Up to 21 different exercise events can be set with different settings of various parameters. Maximum exercise run time is 24 hours. Exerciser features include the following:

Push-button programming control with digital display of settings.

Integral battery operation of time switch when normal control power is unavailable.

Retain "Digital Communication Interface" Paragraph below if digital communication system is used for remote annunciation or for remote annunciation and control. The Kohler MPAC 1200 requires an Ethernet Board accessory to be added for TCP/IP communication.

Digital Communication Interface: Matched to capability of remote annunciator or annunciator and control panel [Modbus 485] [TCP/IP].

Retain "Ethernet Board" Paragraph below when the digital communication interface is required. For Kohler MPAC1200 with Modbus TCP/IP protocol, this option must be selected. This option is standard for the Kohler MPAC1500 controller.

Ethernet Board: RJ-45 connection for communication capability with Modbus TCP/IP protocol.

Retain "Controller Logic Disconnect Switch" Paragraph below for non-service entrance rated transfer switches only.

Controller Logic Disconnect Switch: Two-position switch, mounted inside the enclosure to disconnect three-phase voltage sensing and power to controller without disconnecting the load for use during maintenance and service. The switch has two positions, auto and disconnect. User must manually disable generator prior to placing the controller logic disconnect in OFF position.

STANDARD (OPEN) TRANSITION, CONTACTOR-TYPE TRANSFER SWITCH

Retain this article if Project requires standard, non-bypass isolation transfer switches for loads that can be interrupted during transfer of power. Revise "Standard (Open) Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents.

Standard (Open) Transition Transfer Switches: A break-before-make transfer. The load is disconnected from one normal source before being connected to the alternate emergency source.

Transfer controlled by in-phase monitor and sensors actively monitoring and confirming that both normal and emergency sources are present and acceptable.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Verify availability with manufacturer. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage and Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] [220 V(ac), 50 Hz] [240 V(ac), 60 Hz] [380 V(ac), 60Hz] [380 V(ac), 50 Hz] [400 V(ac), 60 Hz] [400 V(ac), 50 Hz] [416 V(ac), 50 Hz] [440 V(ac), 60 Hz] [480 V(ac), 60 Hz] [600 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral] [4-pole, 4-wire, overlapping neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Open] [Type 1] [Type 3R] [Type 4] [Type 4X] [Type 12], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200 A ratings.

Ampere Rating: [30] [70] [104] [150] [200] [230] [260] [400] [600] [800] [1000] [1200] [1600] [2000] [2600] [3000] [4000] A.

In first subparagraph below, retain front connection for 30-2000A transfer switches. Retain rear connection for 1600-4000A time-based transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" or "In-Phase Monitor" Subparagraph below, or both, to specify alternatives for switching large-motor loads. Coordinate with retained paragraph for transition type. If retaining more than one subparagraph below, or if retaining a subparagraph that is not applicable to all switches, identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS.

In-Phase Monitor: Factory-wired, internal relay controls transfer so contacts close only when the two sources are synchronized in phase and frequency. Relay compares phase relationship and frequency difference between normal and emergency sources and initiate transfer.

PROGRAMMED (DELAYED) TRANSITION, CONTACTOR-TYPE, TRANSFER SWITCH

Retain this article if Project requires delayed transition, non-bypass isolation transfer switches for loads that can be interrupted and still comply with safety requirements. Do not rely on delayed-transition switches to provide power to HID-type lighting if no instant-restrike luminaires provide emergency lighting while the HID restrike. Revise "Programmed (Delayed) Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents.

Programmed (Delayed) Transition Transfer Switches: Pauses or stops in intermediate position to momentarily disconnect both sources, with transition controlled by programming in the automatic transfer-switch controller. Interlocked to prevent the load from being closed on both sources at the same time.

Adjustable Time Delay: For override of normal-source voltage sensing to delay transfer and engine start signals for alternative source. Adjustable from zero to six seconds, and factory set for three seconds.

Sources to be mechanically and electrically interlocked to prevent closing both sources on the load at the same time.

Fully automatic break-before-make operation with center off position.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Verify availability with manufacturer. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage and Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] [220 V(ac), 60 Hz] [240 V(ac), 60 Hz] [380 V(ac), 60 Hz] [380 V(ac), 50 Hz] [400 V(ac), 60 Hz] [400 V(ac), 50 Hz] [416 V(ac), 50 Hz] [440 V, 60 Hz] [480 V(ac), 60 Hz] [600 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Open] [Type 1] [Type 3R] [Type 4] [Type 4X] [Type 12], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200A ratings.

Ampere Rating: [150] [225] [260] [400] [600] [800] [1000] [1200] [1600] [2000] [2600] [3000] [4000] A.

In first paragraph below, retain front connection for 150-2000 A transfer switches. Retain rear connection for 1600-4000 A transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" or "Programmed Neutral Switch Position" Subparagraph below, or both, to specify alternatives for switching large-motor loads. If retaining more than one subparagraph, or if retaining a subparagraph that is not applicable to all switches, identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS. Provide adjustable time delay for reconnecting individual motor loads.

Programmed Neutral Switch Position: Switch operator with programmed neutral position arranged to provide a midpoint between the two working switch positions, with an intentional, adjustable time-controlled pause at midpoint during transfer. Time delay occurs for both transfer directions. Disable pause unless both sources are live.

CLOSED TRANSITION, CONTACTOR TYPE, TRANSFER SWITCH

Retain this article if Project requires closed transition, non-bypass isolation transfer switches for loads intolerant of interruptions or for switching large-motor loads. Coordinate with "Large-Motor-Load Power Transfer" Paragraph and with Drawings. Revise "Automatic Closed-Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents.

Automatic Closed-Transition Transfer Switches: Connect both sources to load momentarily. Transition is controlled by programming in automatic transfer-switch controller.

Fully automatic make-before-break operation when transferring between two available power sources.

Load transfer without interruption, through momentary interconnection of both power sources not exceeding 100 mS.

Integral IEEE 62PL device (parallel timing limit relay) for connection to shunt trip on external source circuit breaker.

Initiation of No-Interruption Transfer: Controlled by in-phase monitor and sensors confirming both sources are present and acceptable.

Retain one of first two subparagraphs below to specify the method of synchronizing the two power sources prior to closing both sources to the load. Consult manufacturer to determine availability of the active control of the generator.

Initiation occurs without active control of generator.

Controls ensure that closed-transition load transfer closure occurs only when the two sources are within plus or minus 5 electrical degrees maximum, and plus or minus 5 percent maximum voltage difference.

Failure of power source serving load initiates automatic break-before-make transfer.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Verify availability with manufacturer. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage and Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] ] [220 V(ac), 50 Hz] [240 V(ac), 60 Hz] [380 V(ac), 60 Hz] [380 V(ac), 50 Hz] [400 V(ac), 60 Hz] [400 V(ac), 50 Hz] [416 V(ac), 50 Hz] [440 V (ac), 60 Hz] [480 V(ac), 60 Hz] [600 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 4X] [Type 12], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200 A ratings.

Ampere Rating: [150] [260] [400] [600] [800] [1000] [1200] [1600] [2000] [2600] [3000] [4000] A.

In first paragraph below, retain front connection for 150-2000 A transfer switches. Retain rear connection for 1600-4000 A time based transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" Subparagraph below to specify method for switching large-motor loads. Identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS. Provide adjustable time delay for reconnecting individual motor loads. Provide relay contacts rated for motor-control circuit inrush and for actual seal currents to be encountered.

STANDARD (OPEN) TRANSITION, CONTACTOR TYPE, BYPASS ISOLATION TRANSFER SWITCH

Retain this article if Project requires standard, bypass isolation transfer switches. Revise "Standard (Open) Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents. Coordinate requirements for bypass/isolation switches with Drawings.

Standard (Open) Transition Transfer Switches: Mechanically and electrically interlocked to prevent the load from being closed on both sources at the same time.

Transfer controlled by in-phase monitor and sensors actively monitoring and confirming both normal and emergency sources are present and acceptable.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Verify availability with manufacturer. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage and Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] ] [220 V(ac), 50 Hz] [240 V(ac), 60 Hz] [380 V(ac), 60 Hz] [380 V(ac), 50 Hz] [400 V(ac), 60 Hz] [400 V(ac), 50 Hz] [416 V(ac), 50 Hz] [440 V(ac), 60 Hz] [480 V(ac), 60 Hz] [600 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral] [4-pole, 4 wire, overlapping neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Type 1] [Type 3R], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200 A ratings.

Ampere Rating: [150] [225] [260] [400] [600] [800] [1000] [1200] [1600] [2000] [2600] [3000] [4000] A.

In first paragraph below, retain front connection for 150-1200 A transfer switches. Retain rear connection for 800-4000 A transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" or "In-Phase Monitor" Subparagraph below, or both, to specify alternatives for switching large-motor loads. If retaining more than one subparagraph, or if retaining a subparagraph that is not applicable to all switches, identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS. Provide adjustable time delay for reconnecting individual motor loads.

In-Phase Monitor: Factory-wired, internal relay controls transfer so contacts close only when the two sources are synchronized in phase and frequency. Relay compares phase relationship and frequency difference between normal and emergency sources and initiate transfer.

PROGRAMMED (DELAYED) TRANSITION, CONTACTOR TYPE, BYPASS ISOLATION TRANSFER SWITCH

Retain this article if Project requires standard, bypass isolation transfer switches. Revise "Programmed Delayed-Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents. Coordinate requirements for bypass/isolation switches with Drawings.

Programmed Delayed-Transition Transfer Switches: Pauses or stops in intermediate position to momentarily disconnect both sources, with transition controlled by programming in the automatic transfer-switch controller. Interlocked to prevent the load from being closed on both sources at the same time.

Adjustable Time Delay: For override of normal-source voltage sensing to delay transfer and engine start signals for alternative source. Adjustable from zero to six seconds, and factory set for three seconds.

Sources to be mechanically and electrically interlocked to prevent closing both sources on the load at the same time.

Fully automatic break-before-make operation with center off position.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Verify availability with manufacturer. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage and Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] ] [220 V(ac), 50 Hz] [240 V(ac), 60 Hz] [380 V(ac), 60 Hz] [380 V(ac), 50 Hz] [400 V(ac), 60 Hz] [400 V(ac), 50 Hz] [416 V(ac), 50 Hz] [440 V(ac), 60 Hz] [480 V(ac), 60 Hz] [600 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral] [4-pole, 4 wire, overlapping neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Type 1] [Type 3R], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200 A ratings.

Ampere Rating: [150] [225] [260] [400] [600] [800] [1000] [1200] [1600] [2000] [2600] [3000] [4000] Amps.

In first subparagraph below, retain front connection for 150-1200 A transfer switches. Retain rear connection for 800-4000 A transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" or "Programmed Neutral Switch Position" Subparagraph below, or both, to specify alternatives for switching large-motor loads. If retaining more than one subparagraph, or if retaining a subparagraph that is not applicable to all switches, identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS. Provide adjustable time delay for reconnecting individual motor loads.

Programmed Neutral Switch Position: Switch operator with programmed neutral position arranged to provide a midpoint between the two working switch positions, with an intentional, adjustable time-controlled pause at midpoint during transfer. Time delay occurs for both transfer directions. Disable pause unless both sources are live.

CLOSED TRANSITION, CONTACTOR TYPE, BYPASS ISOLATION TRANSFER SWITCH

Retain this article if Project requires standard bypass isolation transfer switches. Revise "Automatic Closed-Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents. Coordinate requirements for bypass/isolation switches with Drawings.

Automatic Closed-Transition Transfer Switches: Connect both sources to load momentarily. Transition is controlled by programming in the automatic transfer-switch controller.

Fully automatic make-before-break operation when transferring between two available power sources.

Load transfer without interruption, through momentary interconnection of both power sources not exceeding 100 ms.

Integral IEEE 62PL device (parallel timing limit relay) for connection to shunt trip on external source circuit breaker.

Initiation of No-Interruption Transfer: Controlled by in-phase monitor and sensors confirming both sources are present and acceptable.

Retain one of first two subparagraphs below to specify the method of synchronizing the two power sources prior to closing both sources to the load. Consult manufacturer to determine availability of the active control of the generator.

Initiation occurs without active control of generator.

Controls ensure that closed-transition load transfer closure occurs only when the two sources are within plus or minus 5 electrical degrees maximum, and plus or minus 5 percent maximum voltage difference.

Failure of power source serving load initiates automatic break-before-make transfer.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Verify availability with manufacturer. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage/ Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] ] [220 V(ac), 50 Hz] [240 V(ac), 60 Hz] [380 V(ac), 60 Hz] [380 V(ac), 50 Hz] [400 V(ac), 60 Hz] [400 V(ac), 50 Hz] [416 V(ac), 50 Hz] [440 V(ac), 60 Hz] [480 V(ac), 60 Hz] [600 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral] [4-pole, 4 wire, overlapping neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Type 1] [Type 3R], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200 A ratings.

Ampere Rating: [150] [225] [260] [400] [600] [800] [1000] [1200] [1600] [2000] [2600] [3000] [4000] A.

In first paragraph below, retain front connection for 150-1200 A transfer switches. Retain rear connection for 800-4000 A transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" Subparagraph below to specify method for switching large-motor loads. Identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS. Provide adjustable time delay for reconnecting individual motor loads.

SERVICE ENTRANCE, PROGRAMMED (DELAYED) TRANSITION, BREAKER TYPE, TRANSFER SWITCH

Retain this article if Project requires standard non-bypass isolation transfer switches. Revise "Programmed Delayed-Transition Transfer Switches" Paragraph below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternative," if such terms are used elsewhere in the Construction Documents. Coordinate requirements for bypass/isolation switches with Drawings.

Programmed Delayed-Transition Transfer Switches: Pauses or stops in intermediate position to momentarily disconnect both sources, with transition controlled by programming in the automatic transfer-switch controller. Interlocked to prevent the load from being closed on both sources at the same time.

Adjustable Time Delay: For override of normal-source voltage sensing to delay transfer and engine start signals for alternative source. Adjustable from one second to 60 minutes, and factory set for one second.

Sources to be mechanically and electrically interlocked to prevent closing both sources on the load at the same time.

Retain one of two subparagraphs below to specify the method of transition from alternative power source to primary source after the primary source returns as an acceptable power source.

Fully automatic break-before-make operation with center off position.

Fully automatic break-before-make operation with transfer when two sources have near zero phase difference.

Retain first paragraph below if this Section includes ATS based on circuit-breaker-based products or if design includes fault-current protection internal to transfer switch.

Where transfer switch includes internal fault-current protection, rating of switch and trip unit combination will exceed indicated fault-current value at installation location.

Ground-fault protection equipment must comply with NFPA 70 and be constructed per UL 1008.

Surge protection is required for some emergency alternative power sources. Comply with NFPA 70 for requirements.

Retain first paragraph below for service entrance transfer switches 1200 A and greater.

Energy Reduction Maintenance System is required for power sources. Comply with NFPA 70 for requirements.

Withstand Rating Type: [Specific] [Time-Based] [Short-Time] [Fuse Disconnect].

Retain subparagraph and first option below for standard, UL 1008, short-time withstand ratings to selectively coordinate with overcurrent protection devices. Not available with service entrance rated transfer switches. Selective coordination is required for some emergency-generator-backed, life-safety systems.

Short-time withstand capability for [8] [12] [18] [30] cycles.

Voltage and Frequency Rating: [208 V(ac), 60 Hz] [220 V(ac), 60 Hz] [240 V(ac), 60 Hz] [440 V(ac), 60 Hz] [480 V(ac), 60 Hz].

Configuration Type: [2-pole, 3-wire, solid neutral] [3-pole, 4-wire, solid neutral] [4-pole, 4-wire, switched neutral].

If more than one type of enclosure is used, include a table listing enclosure type for each switch or indicate type on Drawings.

Enclosure Type: General-purpose NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 4X] [Type 12], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

Kohler specific breaker transfer switches are available only with 30-1200 A ratings.

Ampere Rating: [100] [150] [200] [250] [400] [600] [800] [1000] [1200] [1600] [2000] [2500] [3000] [4000] A.

In first paragraph below retain front connection for 30-2000 A transfer switches. Retain rear connection for 1600-4000 A time based transfer switches.

Cable connections accessible via [front] [rear] access.

Large-Motor-Load Power Transfer:

Retain "Motor Disconnect and Timing Relay Controls" or "Programmed Neutral Switch Position" Subparagraph below, or both, to specify alternatives for switching large-motor loads. If retaining more than one subparagraph, or if retaining a subparagraph that is not applicable to all switches, identify applicable characteristics on Drawings.

Motor Disconnect and Timing Relay Controls: Designated starters in loss of power scenario to disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Control connection to motor starters to be through wiring external to ATS. Provide adjustable time delay for reconnecting individual motor loads. Provide relay contacts rated for motor-control circuit inrush and for actual seal currents to be encountered.

Programmed Neutral Switch Position: Switch operator with programmed neutral position arranged to provide a midpoint between the two working switch positions, with an intentional, adjustable time-controlled pause at midpoint during transfer. Time delay occurs for both transfer directions. Disable pause unless both sources are live.

TRANSFER SWITCH ACCESSORIES

Retain "Remote Annunciator System" or "Remote Annunciator and Control System" Paragraph below, or both. Coordinate location of equipment and wiring with Drawings. Coordinate with transfer-switch description, type of engine generator, and Section 260913 "Electrical Power Monitoring and Control." Revise to specify required system features and functions.

Remote Annunciator System:

Source Limitations: Same manufacturer as transfer switch in which installed.

Functional Description: Remote annunciator panel to annunciate conditions for indicated transfer switches.

Annunciation panel display to include the following indicators:

Sources available, as defined by actual pickup and dropout settings of transfer-switch controls.

Switch position.

Switch in test mode.

Failure of communication link.

Annunciator Panel: LED-lamp type with audible signal and silencing switch.

Indicating Lights: Grouped for each transfer switch monitored.

Label each group, indicating transfer switch it monitors, location of switch, and identity of load it serves.

Coordinate description in "Mounting" Subparagraph below with floor plan representation and details on Drawings.

Mounting: Flush, modular, steel cabinet unless otherwise indicated.

Lamp Test: Push-to-test or lamp-test switch on front panel.

Remote Annunciator and Control System:

Source Limitations: Same manufacturer as transfer switch in which installed.

Include the following functions for [single] [multiple] indicated transfer switches:

Indication of sources available, as defined by actual pickup and dropout settings of transfer-switch controls.

Indication of switch position.

Indication of switch in test mode.

Indication of failure of digital communication link.

Key-switch or user-code access to control functions of panel.

Control of switch-test initiation.

Retain one of two subparagraphs below, or delete both.

Control of switch operation in either direction.

Control of time-delay bypass for transfer to normal source.

Retain first subparagraph below with any combination of functions in subparagraphs above.

Malfunction of annunciator, annunciation and control panel, or communication link will not affect functions of ATS. In the event of failure of communication link, ATS automatically reverts to standalone, self-contained operation. Automatic transfer-switch sensing, controlling, or operating function will not depend on remote panel for proper operation.

Remote Annunciation and Control Panel: Solid-state components. Include the following features:

Controls and indicating lights grouped together for each transfer switch.

Label each indicating light control group. Indicate transfer switch it controls, location of switch, and load it serves.

Digital Communication Capability: Matched to that of transfer switches supervised.

Coordinate description in "Mounting" Subparagraph below with floor plan representation and details on Drawings.

Mounting: Flush, modular, steel cabinet unless otherwise indicated.

Padlockable User Interface Cover: Cover to protect the controller user interface from the environment.

Retain "Anti-Condensation Heater" Paragraph below if one or more switches are exposed to high outdoor temperatures and high humidity. Coordinate with Drawings.

Anti-Condensation Heater: Heater strip, sized by manufacturer supplied inside the transfer switch enclosure and controlled by an adjustable humidistat. Humidistat adjustable from 35 to 95 percent relative humidity, factory set at 65 percent. 120 V(ac) power provided from external source with 15 A protective circuit breaker provided internal to transfer switch.

Retain "Surge Protection Device (SPD)" Paragraph below unless a service-rated surge protective device is installed on service equipment between the transfer switch and the utility power connection. Surge protective devices are specified in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

Surge Protection Device (SPD): UL 1449 listed SPD provided for protection of normal source supply with replaceable cartridges to allow replacement of components without disconnecting the normal source supply. 90 dB audible alarm and terminal block for remote alarm contacts provided. SPD to provide L-L, L-N, L-G, and N-G lines protection. LED status indicators integral on the face of the device to indicate operational state.

Input/Output Module: Two programmable inputs and six programmable outputs.

Inputs:

Contact closure.

Current: 5 mA maximum.

Connection Type: Terminal strip.

Wire Size: 14 to 24 AWG.

Maximum Distance: 700 ft. (213 m).

Outputs:

Contact Type: Form C (SPDT).

Contact Rating: 2 A at 30 V(dc) or 500 mA at 125 V(ac).

Connection Type: Terminal strip.

Wire Size: 14 to 24 AWG.

High Current/Voltage I/O Module: Two programmable inputs and three programmable outputs.

Inputs:

Contact closure.

Current: 5 mA maximum.

Connection Type: Terminal strip.

Wire Size: 14 to 24 AWG.

Maximum Distance: 700 ft. (213 m).

Outputs:

Contact Type: Form C (SPDT).

Contact Rating: 12 A at 24 V(dc), 12 A at 250 V(ac), 10 A at 277 V(ac), or 2 A at 480 V(ac).

Connection Type: Terminal strip.

Wire Size: 14-24 AWG.

External Battery Supply Module: External battery to energize ATS controls when no source power is available, allowing extended engine start time delay. Connecting to one or two batteries, at 12 or 24 V(dc) with integral low external battery voltage indication to the transfer switch controller and reverse-polarity protection.

Retain "Alarm Module" Paragraph below based on Project requirements.

Alarm Module: Integral 90 dB audible alarm horn programmable to activate under user selected fault conditions designated through user interface. Audible alarm continues until manually silenced.

Retain one or more of four subparagraphs below based on Project requirements.

Preferred Source Selection for three-source systems.

Provides alarming for non-automatic transfer switch equipped with supervised transfer accessory.

External alarm signal, rated 500 mA at 120 V(ac) or 250 mA at 240 V(ac). Alarm state continues until alarm condition ends.

Chicago Alarm Mode: Audible alarm and indicator light that activate when transfer switch is in emergency position. Audible alarm continues until manually silenced. Alarm state continues until alarm condition ends.

Retain for service-entrance transfer switches only

Line to Neutral Monitoring: Display of AN, BN, and CN RMS voltages in the normal operation menus.

Retain "Load Shed" Paragraph below for programmed and closed transition models if required by Project.

Load Shed: Factory installed control to force transfer of ATS from Emergency to OFF position.

Current Sensing: Measurement and display of load current on all phases with 1 percent accuracy.

Digital Meter: Measurement and display of voltage, current, frequency, and power for both sources, including programmable visual alarms for high and low voltage and high current. A serial, RS-485 port and two auxiliary contacts for external connections and password protected programming menus.

Engine Start Circuit Monitoring Module: Continuously monitoring for wiring faults (open or short circuits) as required by the electrical code NEC 700.10.

SOURCE QUALITY CONTROL

For each test required by UL 1008, provide test confirmation from manufacturer for the following conditions:

General - Normal operation.

Overvoltage.

Undervoltage.

Loss of supply voltage.

Reduction of supply voltage.

Alternative supply voltage or frequency is at minimum acceptable values.

Temperature rise.

Dielectric voltage-withstand; before and after short-circuit test.

Overload.

Endurance.

Short circuit Withstand.

Short circuit Close-On.

Retain first subparagraph below when required. Only available on some models.

Short-time current capability.

Insulating base and supports damage.

Factory tests are an added cost option and may not be available from some manufacturers. Verify requirement with Owner.

Factory Tests: Test and inspect components, assembled switches, and associated equipment in accordance with UL 1008. Ensure proper operation. Check transfer time and voltage, frequency, and time-delay settings for compliance with specified requirements.

Requires CSA certification option.

Perform dielectric strength test complying with UL1008/CSA C22.2-178.

EXECUTION

INSTALLATION

Coordinate location of switches, annunciators, control panels, and associated equipment on Drawings.

Retain "Floor-Mounting Switch" Paragraph below for floor-mounting switches. Coordinate with Drawings.

Floor-Mounting Switch: Anchor to floor by bolting.

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

Install transfer switches on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain first subparagraph below if seismic controls are a project requirement. Coordinate with Drawings.

Comply with requirements for seismic control devices specified in Section 260548.16 "Seismic Controls for Electrical Systems."

Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases.

Provide workspace and clearances required by NFPA 70.

Annunciator and Control Panel Mounting: Flush in wall unless otherwise indicated.

Identify components in accordance with Section 260553 "Identification for Electrical Systems."

Set field-adjustable intervals and delays, relays, and engine exerciser clock.

Comply with NECA 1.

CONNECTIONS

Retain "Wiring to Remote Components" Paragraph below if connections are to remote annunciator, control panel, or motor controller. Coordinate with Drawings.

Wiring to Remote Components: Match type and number of cables and conductors to generator sets, [motor controls, ]control, and communication requirements of transfer switches as recommended by manufacturer. Increase raceway sizes at no additional cost to Owner if necessary to accommodate required wiring.

Retain "Wiring Method" or "Wiring within Enclosures" Paragraph below and coordinate with Drawings. Delete both if wiring method for system is indicated on Drawings.

Wiring Method: Install cables in raceways and cable trays except within electrical enclosures. Conceal raceway and cables except in unfinished spaces.

Comply with requirements for raceways and boxes specified in Section 260533 "Raceways and Boxes for Electrical Systems."

Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.

Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

Retain one of two paragraphs below to reference where twisted pair cable is specified.

Connect twisted pair cable in accordance with Section 260523 "Control-Voltage Electrical Power Cables."

Connect twisted pair cable in accordance with Section 271513 "Communications Copper Horizontal Cabling."

Route and brace conductors in accordance with manufacturer's written instructions[.][ and Section 260529 "Hangers and Supports for Electrical Systems."] Do not obscure manufacturer's markings and labels.

Brace and support equipment in accordance with Section 260548.16 "Seismic Controls for Electrical Systems."

Final connections to equipment to be made with liquidtight, flexible metallic conduit no more than 18 inches (457 mm) in length.

FIELD QUALITY CONTROL

Administrant for Tests and Inspections:

Retain one of four subparagraphs below to specify who administers and performs tests and inspections.

Owner will engage qualified testing agency to administer and perform tests and inspections.

Engage qualified testing agency to administer and perform tests and inspections.

Engage factory-authorized service representative to administer and perform tests and inspections on components, assemblies, and equipment installations, including connections.

Administer and perform tests and inspections[ with assistance of factory-authorized service representative].

Tests and Inspections:

After installing equipment, test for compliance with requirements in accordance with NETA ATS.

Visual and Mechanical Inspection:

Compare equipment nameplate data with Drawings and Specifications.

Inspect physical and mechanical condition.

Inspect anchorage, alignment, grounding, and required clearances.

Verify that the unit is clean.

Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

Verify that manual transfer warnings are attached and visible.

Verify tightness of all control connections.

Inspect bolted electrical connections for high resistance using one of the following methods, or both:

Use of low-resistance ohmmeter.

Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer's published data.

Perform manual transfer operation.

Verify positive mechanical interlocking between normal and alternate sources.

Perform visual and mechanical inspection of surge arresters.

Inspect control power transformers.

Inspect for physical damage, cracked insulation, broken leads, tightness of connections, defective wiring, and overall general condition.

Verify that primary and secondary fuse or circuit-breaker ratings match Drawings.

Verify correct functioning of drawout disconnecting contacts, grounding contacts, and interlocks.

Electrical Tests:

Perform insulation-resistance tests on all control wiring with respect to ground.

Perform a contact/pole-resistance test. Compare measured values with manufacturer's acceptable values.

Verify settings and operation of control devices.

Calibrate and set all relays and timers.

Verify phase rotation, phasing, and synchronized operation.

Perform automatic transfer tests.

Verify correct operation and timing of the following functions:

Normal source voltage-sensing and frequency-sensing relays.

Engine start sequence.

Time delay on transfer.

Alternative source voltage-sensing and frequency-sensing relays.

Automatic transfer operation.

Interlocks and limit switch function.

Time delay and retransfer on normal power restoration.

Engine cool-down and shutdown feature.

Measure insulation resistance phase-to-phase and phase-to-ground with insulation-resistance tester. Include external annunciation and control circuits. Use test voltages and procedure recommended by manufacturer. Comply with manufacturer's specified minimum resistance.

Check for electrical continuity of circuits and for short circuits.

Inspect for physical damage, proper installation and connection, and integrity of barriers, covers, and safety features.

Verify that manual transfer warnings are properly placed.

Perform manual transfer operation.

After energizing circuits, perform each electrical test for transfer switches stated in NETA ATS and demonstrate interlocking sequence and operational function for each switch at least three times.

Simulate power failures of normal source to ATS and retransfer from emergency source with normal source available.

Retain test in first subparagraph below if three-phase undervoltage sensing is specified in Part 2. Test requires advance preparation by testing agency.

Simulate loss of phase-to-ground voltage for each phase of normal source.

Verify time-delay settings.

Verify pickup and dropout voltages by data readout or inspection of control settings.

Test bypass/isolation unit functional modes and related automatic transfer-switch operations.

Usually, require test in first subparagraph below only for critical and extensive installations and for switches rated 1600 A and more in other installations.

Perform contact-resistance test across main contacts and correct values exceeding 500 microhms and values for one pole deviating by more than 50 percent from other poles.

Verify proper sequence and correct timing of automatic engine starting, transfer time delay, retransfer time delay on restoration of normal power, and engine cool-down and shutdown.

Retain "Ground-Fault Tests" Subparagraph below if protective devices for circuits connected to transfer switches include ground-fault protection.

Ground-Fault Tests: Coordinate with testing of ground-fault protective devices for power delivery from both sources.

Verify grounding connections and locations and ratings of sensors.

Observe reaction of circuit-interrupting devices when simulated fault current is applied at sensors. Retain first paragraph below if ATS is associated with generator.

Coordinate tests with tests of generator and run them concurrently.

Report results of tests and inspections in writing. Record adjustable relay settings and measured insulation and contact resistances and time delays. Attach a label or tag to each tested component indicating satisfactory completion of tests.

Prepare test and inspection reports.

Revise "Infrared Scanning" Paragraph below to suit types of switches specified.

Infrared Scanning: After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each switch. Remove all access panels so joints and connections are accessible to portable scanner.

Instrument: Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

Record of Infrared Scanning: Prepare a certified report that identifies switches checked and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

Follow-up Infrared Scanning: Perform an additional follow-up infrared scan of each switch 11 months after date of Substantial Completion.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain transfer switches and related equipment.

Training includes testing ground-fault protective devices and instructions to determine when the ground-fault system will be retested. Include instructions on where ground-fault sensors are located and how to avoid negating the ground-fault protection scheme during testing and circuit modifications.

Retain paragraph below if generators are in Project.

Coordinate this training with that for generator equipment.

END OF SECTION 263600